## Readme
ABOUT THE INFORMATION IN THIS EXCEL TEMPLATE | COST-BENEFIT ANALYSIS RESULTS
Information presented in this excel file has been downloaded from ENTSO-E's TYNDP 2022 projects platform, accessible at https://tyndp2022-project-platform.azurewebsites.net/projectsheets. This excel files contains, for all or part of the projects depending on the filters applied before downloading: - TYNDP 2022 transmission projects data, at project level and at investment level - TYNDP 2022 storage projects data - Results of the cost-benefit analysis performed by ENTSO-E About the data Information presented in the tabs Trans.Projects, Trans.Investments and Stor.Projects was submitted by project promoters. CBA results presented in tabs 2030NT, 2030DE, 2030DEGS and 2040DE are the outcome of the assessment performed by ENTSO-E. Information presented in the tabs Trans.ProjectLevelBenefits and Stor.ProjectLevelBenefits was provided by project promoters. | Tabs 2030NT, 2030DE, 2030DEGS and 2040DE present the results of the cost-benefit analysis performed by ENTSO-E, for each scenario studied in the TYNDP 2022. Refer to the following table for information on each indicator. Results in the tabs 2030NT, etc are for the full area covered by the study (see TYNDP 2022 CBA Implementation Guidelines). Results in tabs 2030NT-ENTSO-E etc are in the ENTSO-E area only (see https://www.entsoe.eu/about/inside-entsoe/members/).
Indicators
| Shortcut | Full name | Indicator | Unit
| ΔSEW | Annual Socio-Economic Welfare (SEW) increase (excluding Energy Not Served cost) | B1 | M€ / year
| ΔSEW_CO2 | Annual Socio-Economic Welfare variation resulting from CO2 emmisions | B1_CO2 | M€ / year
| ΔSEW_RES | Annual Socio-Economic Welfare increase resulting from RES integration | B1_RES | M€ / year
| ΔCO2_market | Annual CO2 varation from market simulation | B2a | ktonnes / year
| ΔCO2_network | Annual CO2 varation due to network losses | B2b | ktonnes / year
| ΔCO2_market_monetised | Annual Societal cost variation resulting from CO2 variation from market simulation | B2a_€ | M€ / year
| ΔCO2_network_monetised | Annual Societal cost variation resulting from CO2 variation from network simulation | B2b_€ | M€ / year
| ΔRES | Annual avoided curtailment (RES integration) | B3 | GWh / year
| ΔRES_MW | Connected RES | B3a | MW
| ΔNOx | Nitrogen oxides | B4a | kg / year
| ΔNH3 | Ammonia | B4b | kg / year
| ΔSO2 | Sulphur dioxide | B4c | kg / year
| ΔPM5 | Particulate matter 5 | B4d | kg / year
For question on TYNDP 2022 data, contact tyndp@entsoe.eu | ΔPM10 | Particulate matter 10 | B4e | kg / year
| ΔNMVOC | Non-methane volatile organic compounds | B4f | kg / year
| Δlosses | Variation of network losses | B5 | GWh / year
| Δlosses_monetised | Variation of network losses monetised | B5_€ | M€ / year
| ΔSoS | Annual reduction in Energy Not Served | B6 | MWh / year
| ΔSoS_monetised | Annual Socio-Economic Welfare increase resulting from reduction in Energy Not Served | B6_€ | M€ / year

## Trans.Projects
TYNDP 2022 - General information on transmission projects | [17 empty] | Needs addressed by the project |  |  |  | Expected transfer capacity increase |  |  | CBA
Project ID | Project Name | Description of the project | Promoters | Country | National development plan(s) | Commissioning Year estimated by the promoter | Status ID 1 : Under Consideration, 2 : In Planning but not permitting, 3 : In permitting, 4 : Under Construction | Is the project cross-border? | Is the project internal? | Type of project - Is it an upgrade of existing infrastructure? | Is the project on the 5th PCI list? | PCI number | Reason for investment clustering | Inclusion in previous TYNDPs | Is the project in the 2027 reference grid? | Is the project in the 2035 reference grid? | Where can one find more information on the project? (ex: project website url) | Needs addressed by the project | Explanation by the promoter on how the project addresses the need | Relevant system needs study results in 2030 (Border - Capacity Increase) | Relevant system needs study results in 2040 (Border or country - Capacity Increase - Storage flexibility - Peaking flexibility) | Border | Transfer capacity increase A-B (MW) | Transfer capacity increase B-A (MW) | Comments on CBA results by the project promoter
1 | RES in north of Portugal | The main objective of this project consists in introducing the network reinforcements that are needed to allow the connection of new RES generation (hydro with pumping and also wind) that is foreseen in the north of Portugal, where the RES potential is high. The project includes a set of new 400 kV OHL that will form a new axis between V. Minho-R. Pena-Feira (PCI 2.16.3). A new 400 kV OHL Pedralva-Sobrado (PCI 2.16.1) is also included in this cluster, in order to ensure the maintenance of the NTC values between PT and ES that were available prior to the connection of these new power plants. | Rede Elétrica Nacional | PT | NDP 1, Portugal, Draft NDP 2022-2031 (2021); Main report, Page 13 (https://www.erse.pt/media/nx3ittiy/pdirt-2022-2031-mar%C3%A7o-2021-relat%C3%B3rio-final.pdf); Apendix 11, page 5 (https://www.erse.pt/media/kdgjy4jl/pdirt-2022-2031-mar%C3%A7o-2021-anexos.pdf) | 2023 | 4 | False | True | New | True | 2.16.3 | Clustering: This project includes a set of new 400 kV OHL that will form a new axis between V. Minho-R. Pena-Feira, ensuring the network capacity to evacuate the new amounts of generation, taking also into consideration the n-1 security criteria. The new substations of R. Pena is also considered in this axis for direct connection of generation. | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | Portuguese National Development Plan: https://www.erse.pt/media/nx3ittiy/pdirt-2022-2031-mar%C3%A7o-2021-relat%C3%B3rio-final.pdf; https://www.erse.pt/media/kdgjy4jl/pdirt-2022-2031-mar%C3%A7o-2021-anexos.pdf Project website https://www.ren.pt/en-GB/o_que_fazemos/projetos_interesse_2017/ PCI page – link to EC platform: https://ec.europa.eu/energy/en/topics/infrastructure/projects-common-interest | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Adequacy needs are identified in Portugal mainly due to the decommissioning of coal power plants in 2021 along with increasing levels of variable RES generation. The integration of Hydro power plants with pumping capabilities (included in this project) are necessary in order to comply with national adequacy standards. Flexibility is the ability of a power system to respond to changes in power demand and generation. Storage facilities such as pumped storage and hydro storage schemes with peak generation are one of the solutions to cope with high power ramps Project for integration of Hydro power plants with pumping |  |  | Internal (Portugal) | 1400 | 1400
4 | Interconnection Portugal-Spain | In order to reach a complete operational Iberian Electricity Market (MIBEL), and strengthen the Internal Energy Market (IEM), the increase of the interconnection between Spain and Portugal is needed. A new OHL 400kV interconnection between Fontefría (Spain) and Ponte de Lima (Portugal). Internal reinforcements complement the cross border section, such as the axis in Spain between Fontefría and Beariz, in order to be able to connect the crossborder project to the existing network, and in Portugal between Ponte de Lima (previously Viana do Castelo) and Vila Nova de Famalicão (previously Vila doConde). This project was included in all the PCI list since 2013 (PCI 2.17). | REN and Red Eléctrica | ES ;PT | Spanish NDP, " Plan de desarrollo de la red de transporte de energia eléctrica. Periodo 2021-2026" , Project Label INT_ESP-POR and Project Sheet in Annex I Page 133 (Main Report in https://www.planificacionelectrica.es/sites/webplani/files/2022-04/REE_Plan_Desarrollo.pdf and interactive project map https://www.planificacionelectrica.es/proyectos) & Portuguese Draft NDP 2022-2031 (2021); Main report, Page 13 (https://www.erse.pt/media/nx3ittiy/pdirt-2022-2031-mar%C3%A7o-2021-relat%C3%B3rio-final.pdf); Apendix 11, page 5 (https://www.erse.pt/media/kdgjy4jl/pdirt-2022-2031-mar%C3%A7o-2021-anexos.pdf) | 2024 | 3 | True | False | New | True | 2.17 | Clustering: the project consists of a set of investments in the same transmission corridor, based on a 400 kV OHL axis linking the substations of Beariz and Fontefría, in Spain, with P. Lima-V. N. Famalicão, in Portugal. These reinforcements are all needed (as they are in series) to achieve the main objectives of the project: reinforcement of the interconnection capacity between Portugal and Spain having in mind the MIBEL targets agreed by the Portuguese and Spanish governments and also to allow Portugal to achieve the 10% interconnection ratio defined by the EC, both contributing for the IEM. | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | Project website http://www.ree.es/es/actividades/gestor-de-la-red-y-transportista/proyectos-de-interes-comun-europeos-pic ; https://www.ren.pt/en-GB/o_que_fazemos/projetos_interesse_2017/ PCI page – link to EC platform https://ec.europa.eu/energy/en/topics/infrastructure/projects-common-interest Other links: Spanish National Development Plan: https://www.planificacionelectrica.es/sites/webplani/files/2022-04/REE_Plan_Desarrollo.pdf and its interactive project map platform: https://www.planificacionelectrica.es/proyectos Portuguese National Development Plan: https://www.erse.pt/media/nx3ittiy/pdirt-2022-2031-mar%C3%A7o-2021-relat%C3%B3rio-final.pdf; https://www.erse.pt/media/kdgjy4jl/pdirt-2022-2031-mar%C3%A7o-2021-anexos.pdf Inter-Governmental agreement (Madrid and Lisbon Declarations) https://ec.europa.eu/energy/sites/ener/files/documents/Madrid%20declaration.pdf ; https://ec.europa.eu/info/sites/info/files/lisbon_declaration_energyinterconnections_final.pdf Constitution of the High Level Group on Interconnections for South West Europe The High Level Group is responsible to prepare a plan to implement the Madrid Declaration and ensure regular monitoring of progress of the projects and provide adequate technical assistance to the Member states. The group will deal with both gas and electricity infrastructure. http://europa.eu/rapid/press-release_IP-15-5187_en.htm XXII Portuguese-Spanish Summit (main conclusions) Main conclusions from the XXII Portuguese-Spanish summit where both governments agreed to continue working on the definition and routes for two new interconnection in order to reach an interconnection capacity of 3000 MW by 2010 between both countries. https://www.madrid.embaixadaportugal.mne.pt/images/Declara%C3%A7%C3%A3o_XXII_Cimeira_Luso-Espanhola.pdf | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | IoSN report shows that for the 2030 NT and 2040NT scenarios the yearly average marginal price difference is higher than the 2€/MWh defined by Interconnection Target Expert Group as threshold for developing new interconnections. In addition, Spanish interconnectors nominal transmission capacity is below 30% of the RES capacity. The increase of interconnection capacity will be essential to cope with the residual load ramps challenge. The increase of interconnection capacity between countries will allow to exchange the power flows from flexibility sources. New interconnections with cross border impact can enable the increase of exchange of balancing energy (Welfare savings through exchanging balancing energy and trough imbalance netting). Balancing energy refers to products such as Replacement Reserve (RR), manual and automatic Frequency Regulation Reserve (FRR). TYNDP shows a reduction of RES spillage considering the increase of interconnection capacity. |  |  | Portugal - Spain | 800 | 1500
16 | Biscay Gulf | The project consists of 370 km HVDC-VSC link (2 bipoles of 1000 MW each) mainly subsea in the Biscay Gulf, between Gatica (Basque Country, ES) and Cubnezais (Aquitaine, FR). Included in the Madrid Declaration, this project aims at improving the interconnection ES-FR. This project was included in all the PCI list since 2013 (PCI 2.7) | Red Eléctrica, Rte | ES ;FR | Spanish NDP "Plan de Desarrollo de la Red de Transporte de Energía Eléctrica. Período 2021-2026", Project Label INT_ESP-FRA_1: Interconexión España-Francia por el Golfo de Vizcaya pg276 https://www.planificacionelectrica.es/sites/webplani/files/2022-06/REE_Plan_Desarrollo.pdf, page 144 and Project Sheet - French NDP, SDDR (Schéma Décennal de Développement du Réseau -Ten Year Network Development Scheme), France, 2019, project n°476, page 441, https://www.rte-france.com/fr/article/evolution-du-reseau-electrique-francais-l-horizon-2035 | 2027 | 3 | True | False | New | True | 2.7 | This project has interdependence with the internal projects P378 and P379 that reinforce the Gatica area in Spain. These internal reinforcements should be commissioned together with the Biscay Gulf. Although the clustering of all projects would have sense, it was not possible due to the CBA methodology clustering rules. A global profitability would have sense considering the 3 projects together. | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | - PCI page – link to EC platform: http://ec.europa.eu/energy/infrastructure/transparency_platform/map-viewer/main.html - Other links Spanish National Development Plan: https://www.planificacionelectrica.es/sites/webplani/files/2022-06/REE_Plan_Desarrollo.pdf and its project sheet platform: https://www.planificacionelectrica.es/proyectos - French National Development Planhttp://www.rte-france.com/fr/article/schema-decennal-de-developpement-de-reseau - Inter-Governmental agreement (Madrid and Lisbon Declarations): https://ec.europa.eu/energy/sites/ener/files/documents/Madrid%20declaration.pdf, https://ec.europa.eu/info/sites/info/files/lisbon_declaration_energyinterconnections_final.pdf - Constitution of the High Level Group on Interconnections for South West Europe: http://europa.eu/rapid/press-release_IP-15-5187_en.htm | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The increase of interconnection capacity will be essential to cope with the residual load ramps challenge. The increase of interconnection capacity between countries will allow to exchange the power flows from flexibility sources. IoSN report shows that for the 2040 time horizon there is need for developing projects in the French-Spanish border as the yearly average marginal price difference is higher than the 2€/MWh defined by Interconnection Target Expert Group as threshold for developing new interconnections. In addition, Spanish interconnectors nominal transmission capacity is below 30% of the national peak load and RES capacity. By increasing interconnection capacity on ES-FR border, the project contributes to enhance flow distribution and RES integration, and to increase exchanges between France and the Iberian Peninsula. TYNDP shows a reduction of RES spillage considering the increase of interconnection capacity in ES-FR border. |  |  | Spain - France | 2200 | 2200
26 | Reschenpass Interconnector Project | New 220kV interconnector between the substations Nauders (AT) and Glorenza (IT). Due to an update of the list of cross-border projects interconnecting Italy with other Member States within 2020, the 2020 interconnection ratio of Italy has been updated accordingly (from previous value of 9% computed by ENTSO-E in TYNDP 2018 to roughly 8%). As the Interconnection level of 10% will not be reached by 2020, Italy is requested to investigate options of further interconnections. | TERNA; APG | AT ;IT | Piano di Sviluppo 2021 – Avanzamento Piani di Sviluppo Precedenti – Avanzamento Nord Est, https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete/pag.95, Italy; APG Netzentwicklungsplan 2019, AT, 2019, 11-12, 48, https://www.apg.at/de/Stromnetz/Netzentwicklung | 2023 | 4 | True | False | New | False |  |  | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | National development plan APG: http://www.apg.at/de/netz/netzausbau/Netzentwicklungsplan National development plan Terna: http://www.terna.it/it-it/sistemaelettrico/pianodisviluppodellarete/pianidisviluppo.aspx | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project contributes to lower the price differentials between Italy north and Austria market zones . This project will contribute to reduce system adequacy deficiencies by increasing transmission capacity. This project helps Italy to reach the 15% interconnection target by 2030 This project will improve the integration of italian RES generation. |  |  | Austria - Italy | 300 | 300
28 | Italy-Montenegro | The Italy-Montenegro interconnection project includes a new HVDC subsea cable between Villanova (Italy) and Lastva (Montenegro) and the DC converter stations. The second HVDC module (600 MW) of the Italy-Montenegro interconnection project is strictly correlated with the Transbalkan (project 227) and the Mid Continental East (project 144) corridors, and therefore contributes significantly to enable the usage of an increased transmission capacity between Italy and South-Eastern European Countries (especially Romania and Bulgaria) | Terna, CGES | IT ;ME | Piano di Sviluppo 2021 – Avanzamento Piani di Sviluppo Precedenti – Avanzamento Centro Sud, Italy, 2021, ID: 401-P, 62, https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete | 2026 | 4 | True | False | New | False |  |  | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | True | PCI information: https://www.terna.it/it-it/sistemaelettrico/pianodisviluppodellarete/progettidiinteressecomune.aspx Link to the last release of the Italian National Development Plan: http://www.terna.it/it-it/sistemaelettrico/pianodisviluppodellarete/pianidisviluppo.aspx | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project contributes to lowering the price differentials between Italian market zones and Montenegro This project will contribute to reduce system adequacy deficiencies by increasing transmission capacity This project will help to solve important congestions among Italian transmission grid This project will improve the integration of italian RES generation | Italy - Montenegro - 1100 | Italy - Montenegro - 600 - Italy - - 1000 - 5000 | Italy - Montenegro | 600 | 600
29 | Italy-Tunisia | The project consists in a new interconnection between Tunisia and Sicily to be realized through an HVDC submarine cable. The realization of the project is supported by the Italian and Tunisian Governments to increase the interconnection capacity of the Euro-Mediterranean system. Moreover, the project will contribute to reduce, under specific conditions, present and future limitations to the power exchanges on the northern Italian border, with France, Switzerland, Austria and Slovenia, and therefore it will allow to significantly increase the transmission capacity and its exploitation by at least 500 MW on that boundary. | Terna, STEG | IT ;TN | Piano di Sviluppo 2021 – Avanzamento Piani di Sviluppo Precedenti – Avanzamento Centro Sud, Italy, 2021, ID: 601-I, Pag.33, https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete | 2028 | 3 | True | False | New | True | 2.33 |  | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | The project has recently received funds for detailed design necessary for the permitting phase Link to the last release of the Italian National Development Plan http://www.terna.it/en-gb/sistemaelettrico/pianodisviluppodellarete.aspx | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project contributes to lowering the price differentials between Italian and Tunisia market zones This project will contribute to reduce system adequacy deficiencies by increasing transmission capacity This project will improve the integration of italian RES generation | Italy - Tunisia - 600 | Italy - Tunisia - 600 - Italy - - 1000 - 5000 | Italy - Tunisia | 600 | 600
33 | Central Northern Italy | The project consists in the strengthening of interconnection between the northern and the central part of Italy. It will involve the upgrading of existing 220 kV over-head line to 400 kV between Colunga and Calenzano substations as well as the removing of limitations on the existing 220 kV network in Central Italy | Terna SpA | IT | Piano di Sviluppo 2021 – Avanzamento Piani di Sviluppo Precedenti – Avanzamento Nord Est https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete/Pag.100-102, Italy | 2026 | 4 | False | True | Upgrade | False |  | The two investments will closely contribute to reduce congestions and guarantee a major market integration between Italy-North and Italy Center. General comment for all projects: the scope of TYNDP project analysis is broader than national. This was done in line with TYNDP 2020 and the possibility of de-clustering projects will be considered in the future. | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | "Link to the last release of the Italian National Development Plan http://www.terna.it/en-gb/sistemaelettrico/pianodisviluppodellarete.aspx" | Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | In case of failure of the OHL along the Adriatic or Thyrrenic coast the upgraded lines will improve transient stability. The new line will allow congestion reduction on the North Center-Northern border, in order to transport the foreign import to the local loads and to integrate the southern renewable production. |  |  | Internal (Italy) | 400 | 400
35 | CZ Southwest-east corridor | A corridor of internal 400 kV overhead lines inside the Czech Republic connecting existing 420 kV substations between Prestice, Kocin and Mirovka in the southwest-east direction. The project consists of building a new AC 400 kV overhead line which connects 420 kV substations Kocin and Mirovka with double circuit line of about 120.5 km length and a nominal transmission capacity of 2 x 2445 A, building a AC 400 kV overhead lines that involves changing of a 400 kV existing single-circuit line to double-circuit line with a nominal capacity of 2 x 2445 A between Kocin and Prestice. | CEPS | CZ | Ten-year investment plan for the development of the TS 2021 – 2030, CZ, 2021, V406/407–New KOC–HBM Line and V432/429–Line Doubling, 128 pg., https://www.ceps.cz/en/transmission-system-development | 2028 | 3 | False | True | MostlyNew | True | 3.11.3 and 3.11.4 | Project 35 that contains investment items 313 and 315 altogether with Project 200 that contains investment item 308 (item 309 was already commissioned) forms a geographically continuous (uninterrupted) network corridor from a new 420 kV substation Vernerov (already commissioned at the end of 2017), through a new 420 kV substation Vitkov (which is also already commissioned at the end of 2020), existing 420 kV substation Prestice, existing 420 kV substation Kocin and ending up to the existing substation 420 kV Mirovka. It is actually what is referred as a “convoy lines” or "sequential projects" with all 4 involved 400 kV overhead lines (investment 308 (Vernerov-Vitkov), 309 (Vitkov-Prestice), 315 (Prestice-Kocin) and 313 (Kocin-Mirovka)) connected in series forming a corridor from the northern-western part of the Czech grid related to the DE-CZ border into the south and eastern direction towards the CZ-SK and CZ-AT borders. | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | True | Information about Czech development plan and PCI projects can be found on the following links below on the CEPS website: https://www.ceps.cz/en/transmission-system-development https://www.ceps.cz/en/pci-projects-of-common-interest | Infrastructure to reduce price differentials between EU and/or non-EU countries Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project helps to decrease the curtailed energy in Germany due to extra market transfers (increase of NTC) on the profile DE - CZ which lead to reduction of marginal price. The project contains the upgrade of existing 220 kV lines to 400 kV lines which will reduce infrastructure vulnerability and therefore ensure reliable and secure operation of the grid. This project besides the increase of NTC also consists of reinforcement of internal lines and therefore facilitates the future need for cross-border flows. The project is aiming at facilitation of the power flows from the RES generation in the northern part of Europe and western part of CZ therefore promotes RES integration. | Czech Republic - Germany - 1000 | Czech Republic - Germany - 1000 - Germany - - 5000 - 10000 | Czechia - Germany | 500 | 500
40 | Belgium-Luxembourg-Germany: long-term perspective | An increase of transfer capacity across the BE-LU-DE corridor is envisioned towards the 2040 time horizon. Further studies will determine the appropriate implementation option and timing, taking into account: - the expected evolution on the LU-DE border as presented in project 328 Project motivation: This project increases the degree of interconnectivity between the Belgian - Luxemburg - German corridor. The possibility of higher market exchanges between bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. | Amprion, Creos, Elia | BE ;DE ;LU | NDP1, Belgium, 2020-2030, §4.5.1, NDP2, Luxemburg, 2040, Scenario report 2040 p.43 ( 2nd February 2018) | 2040 | 1 | True | False | New | False |  |  | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | False | More information about the project can be found following this link: - National Development Plan: https://www.elia.be/-/media/project/elia/elia-site/infra-and-projects/investment-plans/federal-development-plan-2020-2030/nl/20190516_federaal-ontwikkelingsplan_nl.pdf?la=en | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Project increases the degree of interconnectivity between the Belgian - Luxemburg - German corridor and allows higher market exchanges leading to higher price convergence. Project increases the degree of interconnectivity between the Belgian - Luxemburg - German corridor and allows higher market exchanges leading to higher price convergence RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manne | Belgium - Luxemburg - 500 Luxemburg - Germany - 400 | Belgium - Luxemburg - 500 - Luxemburg - Germany - 400 - Germany - - 5000 - 10000 Luxemburg - - <1000 Belgium - - <1000 | Belgium - Luxembourg | 500 | 500
47 | Westtirol (AT) - Vöhringen (DE) | This project will increase the current power exchange capacity between Austria and Germany by an upgrade of the existing overhead line Vöhringen (DE) - Westtirol (AT) to 380 kV and the extension of existing and errection of new 380-kV-substations including 380/110-kV-transformers. | Amprion, Austrian Power Grid | AT ;DE | Germany: Netzentwicklungsplan 2035 Version 2021, Project P74, p.457, Austria: APG Netzentwicklungsplan 2021, AT, 2021, 13-2, 48, https://www.apg.at/en/Stromnetz/Netzentwicklung | 2030 | 2 | True | False | Upgrade | False |  |  | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | True | http://www.apg.at/en/netz/netzausbau/Netzentwicklungsplan https://www.netzentwicklungsplan.de/de/projekte/projekte-nep-2035-2021 The project was part of the previous TYNDP 2020, Link to the Website: https://tyndp2020-project-platform.azurewebsites.net/projectsheets/transmission/47 | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Increase of German interconnection level. Better utilisation of existing and future pump storage power plants by improved transport capacities. Connecting German RES power with pump storages in Austria. | Austria - Germany - 3100 | Austria - Germany - 3100 - Austria - - <1000 Germany - - 5000 - 10000 | Austria - Germany | 600 | 600
81 | North South Interconnector | A new 400 kV interconnector between Woodland in Ireland and Turleenan in Northern Ireland. | Eirgrid, SONI | GB ;IE | • Transmission Development Plan Northern Ireland 2020-2029, page 73: https://www.soni.ltd.uk/media/documents/SONI-Transmission-Development-Plan-Northern-Ireland-2020-2029.pdf • Transmission Development Plan Ireland 2019-2028, page 40: https://www.eirgridgroup.com/site-files/library/EirGrid/TDP-2019-2028-Final-For-Publication.pdf, All-Island Generation Capacity Statement 2021-2030, p.41: https://www.eirgridgroup.com/site-files/library/EirGrid/208281-All-Island-Generation-Capacity-Statement-LR13A.pdf | 2025 | 3 | True | False | New | False |  |  | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | Project website: http://www.eirgridgroup.com/the-grid/projects/north-south/the-project/ This circuit will establish a second interconnector between Ireland and Northern Ireland, effectively eliminating the ongoing risk of system separation, thus allowing an increased transfer capacity. The project has received the required consents in both jurisdictions. The project will be implemented by the respective transmission asset owners with an expected completion date of 2025. | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The new interconnector will increase the capacity, and the reliability, of interconnection between the Ireland and Northern Ireland networks. This will allow the two independent networks to operate together as if they were one system for the mutual benefit of residents and businesses in both jurisdictions. The new interconnector will increase the capacity, and the reliability, of interconnection between the Ireland and Northern Ireland networks. This will allow the two independent networks to operate together as if they were one system for the mutual benefit of residents and businesses in both jurisdictions. The increase in interconnection capacity will effectively eliminate current restrictions in cross border support in the event of a shortage of electricity in one jurisdiction, thus enhancing the security of electricity supply throughout the island of Ireland. The increase in interconnection capacity between Ireland and Northern Ireland (because of this interconnection) will facilitate further and greater connection of wind generation in both parts of the island which will help achieve Ireland’s renewable energy targets. |  |  | Ireland - Northern Ireland | 950 | 900
85 | Integration of RES in Alentejo | The main objective of this project consists in introducing the network reinforcements that are needed to allow the connection of new RES generation (mostly solar but also some wind) that is foreseen for the south region of Portugal, where the solar potential is considerably high. The project includes two new 400 kV OHL that will constitute a new axis between F. Alentejo-Ourique-Tavira substations. It is also included the expansion of the Ourique substation to include the 400 kV voltage level and a new 400KV OHL Alqueva-Divor. | Rede Elétrica Nacional | PT | NDP 1, Portugal, Draft NDP 2022-2031 (2021); Main report, Page 13 (https://www.erse.pt/media/nx3ittiy/pdirt-2022-2031-mar%C3%A7o-2021-relat%C3%B3rio-final.pdf); Apendix 11, page 5 (https://www.erse.pt/media/kdgjy4jl/pdirt-2022-2031-mar%C3%A7o-2021-anexos.pdf) | 2022 | 3 | False | True | MostlyUpgrade | False |  | Clustering: the project consists of a new axis connecting Ferreira do Alentejo and Tavira substations, passing through an intermediate substation (Ourique) that will need to be expanded to include the 400 kV voltage level. All these investments are in series so a lack of any of them will not allow to get the desired GTC increase of the project. Also a new 400 OHL Alqueva-Divor is included in this cluster in order to increase and allow the maximum utilization of the potential of the main investment. | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | Portuguese National Development Plan: https://www.erse.pt/media/nx3ittiy/pdirt-2022-2031-mar%C3%A7o-2021-relat%C3%B3rio-final.pdf; https://www.erse.pt/media/kdgjy4jl/pdirt-2022-2031-mar%C3%A7o-2021-anexos.pdf Video: https://www.youtube.com/watch?v=RihzW55870c | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | TYNDP 2018 and 2020 System Needs study showed high level of congestion in the network resulting from the integration of RES (mainly Solar) in the south of Portugal where the solar potential is considerably high. Project for integration of RES (mainly Solar). |  |  | Internal (Portugal) | 1000 | 1000
94 | GerPol Improvements | The new Phase Shifting Transformers (PST) in Mikulowa on the 400 KV double line Mikulowa–Hagenwerder were already finally commissioned in June 2016. The first two PST in Vierraden have been commissioned in August 2018. The updated 400 kV double line Krajnik – Vierraden is in operation with one system and these two PST in series. On the German side there is a link to the existing 220 kV lines using two 380/220 kV transformers as an intermediate step. Two further Phase Shifting Transformers (380 kV/380 kV) will replace these two 380/220 kV transformers in substation Vierraden after the upgrade of the existing German Uckermark-line to 380 kV. This necessary upgrade of the connecting Uckermark-line is delayed due to court case against the building permission. The court case has been settled in July 2022 and the upgrade of the Uckermark-line is proceeding. | 50Hertz | DE ;PL | German NEP2035, version 2021, 2nd draft, Germany, 2021, project 50HzT-P128, p. 262-264; | 2025 | 4 | True | False | Upgrade | False |  |  | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Finalization of the project GerPol Improvements allows to increase cross-border capacity on the Polish-German border and thus allows to exchange more energy. Project contributes to mitigate the risk of adequacy deficiencies in Germany and Poland by connecting areas with different mix of generation. This project contributes a reduction of unscheduled flows DE-PL, PL-CZ and PL-SK by increasing the controllability of the power flow on the DE-PL border. This project enables the integration of additional RES in the area of western and north-western Poland as well as in the eastern part of Germany. |  |  | Germany - Poland | 500 | 1500
103 | Reinforcements Ring NL phase I | Upgrade of existing 380kV circuits in the Dutch main ring from 2,5 kA to 4 kA. | TenneT NL | NL | Investeringsplan Net op land 2020 - 2029, Netherlands, 2020, page 86, https://www.tennet.eu/fileadmin/user_upload/Company/Publications/Investeringsplannen/IP2020_NOL_201001.pdf | 2025 | 4 | False | True | Upgrade | False |  | The upgrade of the main 380 kV ring in NL is needed in order increase the DE-NL border NTC to the agreed value. The upgrade of the ring is split into different phases (investments), with different commissioning dates. The main constraint is the Diemen-Lelystad-Ens axis and therefore its upgrade is indicated as the main investment. Without the upgrade of the other lines (Krimpen-Geertruidenberg, Ens-Zwolle and Maasbracht-Eindhoven), the full potential of the project cannot be achieved. | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | All investements in this project are related to the upgrade of the main 380 kV ring structure in the Netherlands. https://www.tennet.eu/nl/ons-hoogspanningsnet/onshore-projecten-nederland/beter-benutten-bestaande-380kv/ | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Upgrade of the internal grid via this project will help facilitated increase of cross-border exchange capacity between different bidding zones reducing thus the price differentials The upgrade of the internal grid will solve congestions due to new power flow patterns for which the grid was not designed for. Connection of high volumes of RES in the future will create high flows for which the grid was not designed for. Upgrading the grid via this project will help transport power from the generation sites to the load centers |  |  | Germany - Netherlands | 600 | 600
107 | Celtic Interconnector | Celtic Interconnector will be the first interconnection between Ireland and France. A survey of the route of the HVDC (VSC) link with 700 MW capacity has been done from the southern coast of Ireland to La Martyre (Finistère) in France. Motivation for the project : The CELTIC project will improve security of supply in both Ireland and France. It will facilitate increased electricity trading that will result in increased competition and downward pressure on electricity prices. The CELTIC project will also support the development of renewable sources of energy. | Eirgrid, RTE | FR ;IE | NDP1, Ireland, n°107, 2016, page 92 - NDP2, France, SDDR (Schéma Décennal de Développement du Réseau -Ten Year Network Development Scheme), 2019, project n°437, page 442, https://www.rte-france.com/en/analyses-trends-and-perspectives/ten-year-network-development-plan#Documents | 2027 | 3 | True | False | New | True | 1.6 |  | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | More information can be found on Project Websites : https://www.rte-france.com/fr/projet/celtic-interconnector-projet-d-interconnexion-entre-la-france-et-l-irlande and http://www.eirgridgroup.com/the-grid/projects/celtic-interconnector/the-project/. The project is also part of both RTE and Eirgrid National Development plans. In addition, CELTIC project has been confirmed on 31 October 2019 as a Project of Common Interest 1.6 in the priority corridor Northern Seas Offshore Grid (NSOG)." | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Figures 2.12 and 2.13 of IoSN 2020 Report show that average marginal price difference would be higher than 10€/MWh between France and Ireland in future scenarios if no investment is done, and only between 5 and 10€/MWh with the investment. Based on IoSN 2020 Report, 15% IC-target requires higher cross border transmission capacity. This project P107 contributes to satisfy this need (especially for Ireland, by increasing the transmission capacity while the installed RES generation is going higher too). IoSN 2020 Report Chapter 5 (Flexibility aspect, Transient and voltage stability related aspects): the ramp increases from NT2025 to NT2040. The project allows Ireland to take benefits from the more stable continental grid, participates in reactive power management and frequency management by quickly changing its active power. IoSN 2020 Report, figures 2.8-2.11: main drivers of NT scenarios are better access to RES generation (avoiding curtailment) which replaces expensive thermal generation. Figures 2.2-2.3: in Ireland, curtailment decreases by half with the IoSN SEW needs in 2030 compared to 2020. Same for 2040 compared to 2025. | France - Ireland - 700 | France - Ireland - 700 - France - - 1000 - 5000 Ireland - - <1000 | France - Ireland | 700 | 700
111 | Aurora line (3rd AC Finland-Sweden north) | Third AC 400 kV overhead line interconnector between Finland north and Sweden SE1. Strengthening the AC connection between Finland and Sweden is necessary due to market needs, security of supply in the Nordics, new RES generation and larger conventional units. | Fingrid, Svenska Kraftnät | FI ;SE | Kantaverkon kehittämissuunnitelma 2022-2031, page 15, available here: https://www.fingrid.fi/kantaverkko/kehittaminen/kantaverkon-kehittamissuunnitelma/kantaverkon-kehittamissuunnitelma-2022-2031/ (currently in Finnish, will be available in English later); System Development Plan 2020-2029, Sweden, 2019, p.81: Availble online: {https://www.svk.se/siteassets/om-oss/rapporter/2019/systemutvecklingsplan2020-2029.pdf} | 2025 | 3 | True | False | New | True | 4.10.1 and 4.10.2 | Investment 1710 is needed to get the full capacity of investment 396 | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | Wep page of the project: https://www.fingrid.fi/en/grid/construction/cross-border-connections/Aurora-Line-new-finland-sweden-interconnector/#41cebfa7 Svenska kraftnät has published a grid investment plan in 2019. The purpose of the plan is to be an investment plan for the following ten years, 2020-2029. The report is available as follows: System Development Plan 2020-2029, Sweden, 2019, p.81: Availble online: {https://www.svk.se/siteassets/om-oss/rapporter/2019/systemutvecklingsplan2020-2029.pdf} Fingrid has published a national development plan in 2022-2031. The investment plan presents a detailed look of the projects. The plan is available in Finnish: https://www.fingrid.fi/kantaverkko/kehittaminen/kantaverkon-kehittamissuunnitelma/kantaverkon-kehittamissuunnitelma-2022-2031/ | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. | Adds market capacity 800/900 MW. Improves Finnish power balance after Russia suspended electricity and gas delivery to Finland. Also strengthens the connection of Finland with the other Nordic countries. Adds market capacity 800/900 MW. Contributes to all three interconnection targets. Strengthens the connection of Finland and Sweden and improves stability of the Nordic synchronous system. | Finland - Sweden - 1700 | Finland - Sweden - 2500 - | Finland - Sweden | 900 | 800
120 | Belgian Modular Offshore Grid II (MOG II) | MOG II aims at centralizing the offshore wind farms in an offshore hub and transporting offshore energy to a substation along a new 380kV corridor Stevin-Avelgem (project 329). Number and size of hubs is subject to ongoing studies - whereas current working hypothesis indicate a total capacity ranging from 2,1 GW to 3,5 GW. Structure, capacity, timing are all subject to a final decision on the total offshore wind capacity to be connected in the Princess Elisabeth Zone defined in the Belgian Marine Spatial Plan 2020-2026. Project consists of offshore grid investments that allows to connect the new wave of offshore energy to the mainland (on top of the existing 2,3GW) in an efficient, reliable and future-proof way and strongly facilitates RES integration in Belgium. Belgian law approved on 4th of April 2019 (DOC 54 3581/008) creates a legal framework for a second Modular Offshore Grid. Additional offshore (wind) capacity is expected to be connected to the onshore grid partly via a HVDC and a AC system. Such a setup offers potential synergies with future (hybrid) interconnectors (eg. project 121 and 1092). | Elia | BE | NDP1, Belgium, 2020-2030, §4.3.2 | 2028 | 2 | False | True | New | False |  | Both investments will be jointly built offshore and serve the same purpose of integrating the offshore energy to the mainland and facilitates potential future further integration offshore. | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | More information can be found following these links: - Project site: https://www.elia.be/en/infrastructure-and-projects/infrastructure-projects/mog-ii - National Development Plan: https://www.elia.be/-/media/project/elia/elia-site/infra-and-projects/investment-plans/federal-development-plan-2020-2030/nl/20190516_federaal-ontwikkelingsplan_nl.pdf?la=en | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Project consists of offshore grid investments that allows to connect a new wave of offshore energy to the mainland (3,5GW on top of existing 2,3GW OWF) in an efficient and reliable way - hence strongly facilitates RES integration for Belgium. |  |  | Internal (Belgium) (AC) Internal (Belgium) (DC) | 2100 1400 | 2100 1400
121 | Nautilus: multi-purpose interconnector Belgium - UK | This project considers the possibility of a multi-purpose HVDC interconnection between GB and Belgium, that combines the benefits of connecting electricity markets and offshore wind generation in Belgium and/or Great Britain. The capacity of the interconnection is still under review, but is likely to be in the range of 1 GW – 2GW, with the reference NTC contribution being 1,4GW at this stage. Increasing commercial market exchange capacity between Belgian and Great-Britain will increase overall social welfare. An important security of supply contribution is also achieved through implementation of this project, both from avoided alternative investments as from a reduction in loss of load expectancy. Such adequacy contribution can be linked to the decreasing figures of installed conventional generation and increasing RES. Additionally, integrating offshore wind capacity on to the interconnector could lead to increased benefits and/or investment savings. Finally, benefits related to integration of cross-border redispatching, balancing markets, and exchange or sharing of ancillary services across the HVDC interconnection between synchronous areas can be obtained. | Elia, National Grid | BE ;GB | NDP1, Belgium, 2020-2030, §4.2.3.3;NDP2, UK, 2017, p.23 §2.3 | 2029 | 2 | True | False | New | False |  |  | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | True | More information on the project can be found following these links: - Project site: https://www.elia.be/en/infrastructure-and-projects/infrastructure-projects/nautilus - National Development Plan: https://www.elia.be/-/media/project/elia/elia-site/infra-and-projects/investment-plans/federal-development-plan-2020-2030/nl/20190516_federaal-ontwikkelingsplan_nl.pdf?la=en | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between the Belgian and UK bidding zone and possibility of higher market exchanges which leads to higher price convergence. This is also a key trigger of the 2030 ITEG targets. This project has an important adequacy contribution due to decreasing figures of installed conventionals and increasing RES. This is also a key trigger of the 2030 ITEG targets This interconnector project between Belgium and UK is designed as a HVDC-link. The full controllability of the HVDC link facilitates the balancing of active and reactive power in the Belgian and UK grid RES integration implies higher flows within & between AC-grid(s) and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. This is also a key trigger of the 2030 ITEG targets. | Belgium - UK - 1400 | Belgium UK - 1400 - Belgium - - <1000 | Belgium - United Kingdom | 1400 | 1400
123 | LitPol Link Stage 2 | Construction of new 400 kV AC double-circuit OHL line with a length of 108 km and capacity of 2x1870 MVA between Ostrołęka and Stanisławów. Temporary one circuit will use part of the existing 220 kV single-circuit line between Ostrołęka and Miłosna. In one circuit of 400 kV line, the Wyszków substation will be constructed. After the construction of 400 kV line, the 220 kV line will be disconnected. Extension of 400 kV Ostrołęka and Stanisławów substations for connection of new Ostrołęka - Stanisławów line. The project is already finished on the Lithuanian side. | Polskie Sieci Elektroenergetyczne S.A. | LT ;PL | "Development Plan for meeting the current and future electricity demand for 2021-2030", Poland, Year 2020, Project II.2, II.3, Page 41, https://www.pse.pl/documents/31287/84e7121a-e0c0-4dee-ab2c-61bba30f4646?safeargs=646f776e6c6f61643d74727565. | 2023 | 4 | False | True | MostlyNew | True | 4.5.2 | The investment is the last element of the project which is crucial for a stable connection of the LitPol Link within the Polish transmission system, especially in the conditions of synchronous operation of this connection. | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | Link to PSE S.A. Development Plan: https://www.pse.pl/documents/31287/84e7121a-e0c0-4dee-ab2c-61bba30f4646?safeargs=646f776e6c6f61643d74727565 Description of PCI projects on PSE website: https://www.pse.pl/obszary-dzialalnosci/inwestycje-infrastrukturalne/informacje-o-projektach-wspolnego-zainsteresowania-pci?safeargs=696e686572697452656469726563743d74727565 3rd PCI list: https://ec.europa.eu/energy/sites/ener/files/documents/annex_to_pci_list_final_2017_en.pdf 4th PCI list: https://ec.europa.eu/energy/sites/ener/files/c_2019_7772_1_annex.pdf Link to project web page:http://liniaostrolekastanislawow.pl/ |  |  |  |  | Lithuania - Poland | 500 | 500
124 | NordBalt phase 2 | Second phase includes the internal network reinforcement in Sweden, a key investment to accomplish full utilization of the NordBalt cable between Lithuania and Sweden. The rest of internal investments already commissioned. | AST, Svenska Kraftnat, Litgrid AB | LT ;LV ;SE | System Development Plan 2020-2029, Sweden, 2019, p. 85 | 2027 | 3 | True | False | New | True | 4.4.2 | The investment Grobina (LV) - Imanta (LV) in Latvia is commissioned. | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | False | Svenska kraftnät has published a national development plan in 2019. The purpose of the plan is to be an investment plan for the following ten years, 2020-2029. The investment plan presents a detailed look of the projects Svenska kraftnät intends to realize under the stated time period. The plan is available in Swedish through the following link: https://www.svk.se/siteassets/om-oss/rapporter/2019/systemutvecklingsplan2020-2029.pdf (Swedish) | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | Internal reinforcement inside Sweden to utilize the interconnector between Lithuania and Sweden. To be able to fully utilize the interconnector between Lithuania and Sweden. |  |  | Lithuania- Sweden | 0 | 0
126 | SE North-south short-term reinforcements | Reactive measures in substations and series compensations in order to increase capacity between SE2 and SE3. Replacement of ageing overhead lines that also will contribute to the increased capacity. | Svenska Kraftnät | SE | 10-Year Grid Investment Plan 2020-2029 , Sweden, 2020, p. 12. {Available online: https://www.svk.se/siteassets/om-oss/rapporter/2020/10-year-development-plan-2020-2029.pdf} | 2035 | 2 | False | True | Upgrade | False |  |  | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | Svenska kraftnät has published a national development plan in 2019. The purpose of the plan is to be an investment plan for the following ten years, 2020-2029. The investment plan presents a detailed look of the projects Svenska kraftnät intends to realize under the stated time period. The plan is available in Swedish through the following link: https://www.svk.se/siteassets/om-oss/rapporter/2019/systemutvecklingsplan2020-2029.pdf (Swedish) | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) | Increase the power transfer capcaity among Swedish price zones. Improve reactive power compensation and increase the voltage stability. Replacement of ageing overhead lines that also will contribute to the increased capacity and reserve capacity. |  |  | Internal (Sweden) | 2000 | 2000
127 | Central Southern Italy | The project consists in the reinforcement of southern Italy 400 kV network through new 400 kV lines. The activities will involve the network portions between the substation of Villanova and Foggia, Deliceto and Bisaccia | Terna | IT | Piano di Sviluppo 2021 – Avanzamento Piani di Sviluppo Precedenti – Avanzamento Centro Sud https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete/pag.66-129 | 2027 | 3 | False | True | New | False |  | The two investments will closely contribute to reduce congestions and guarantee a major market integration between Italy-center South and Italy South. General comment for all projects: the scope of TYNDP project analysis is broader than national. This was done in line with TYNDP 2020 and the possibility of de-clustering projects will be considered in the future. | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | Link to the last release of the Italian National Development Plan http://www.terna.it/en-gb/sistemaelettrico/pianodisviluppodellarete.aspx | Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | In case of failure of the first OHL Foggia-Villanova the new line will improve transient stability. The new line will allow congestion reduction in the Southern-Northern border, and the integration of the local renewable production. Reduction of expected RES curtailment |  |  | Italian Northern border or Italy-Greece Internal (Italy) | 500 1000 | 500 1000
130 | HVDC SuedOstLink Wolmirstedt to area Isar | 2 GW HVDC-connection from North-East Germany (Area of Wolmirstedt), an area with high installed capacities of RES, to the South of Bavaria (area of Isar), an area with high consumption and connections to storage capabilities. | 50Hertz, TenneT DE | DE | NEP Strom 2035 version 2021, page 396 (German National Development Plan) | 2025 | 3 | False | True | New | True | 3.12 |  | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | Permitting status in the TYNDP reflects the fact, that the necessity of the project is approved by the NRA and is German Law (so called Bundesbedarfsplangesetz, listed as project No. 5). Therefore the realization is mandatory. In addition, according to German law, the permitting process has already started. http://www.gesetze-im-internet.de/bbplg/BBPlG.pdf (Page 4, Project Nr. 5) https://www.netzausbau.de/leitungsvorhaben/de.html?cms_map=2 German grid development plan: http://www.netzentwicklungsplan.de/en Project Homepage: http://www.50hertz.com/en/Grid-Extension/Projects/SuedOstLink https://www.tennet.eu/de/unser-netz/onshore-projekte-deutschland/suedostlink/ 3rd PCI-list: https://ec.europa.eu/energy/sites/ener/files/documents/annex_to_pci_list_final_2017_en.pdf 4th PCI-list: https://ec.europa.eu/energy/sites/ener/files/c_2019_7772_1_annex.pdf | Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Infrastructure improves system flexibility and stability. Controllable HVDC connections stabilize the increasingly stressed German system. DC power lines can provide better controllability in the power grid and support especially voltage stability in the system, as the converters can provide both capacitive and inductive reactive power. In situations with high wind infeed or high pan-European market driven flows, unscheduled load flows from North of Germany over Poland and Czech Republic to Bavaria or Austria can occur. The project will reduce unintended load flows significantly and will relieve the transmission grids of neighboring countries. The project will connect the North-East of Germany, a region with a high amont of renewables covering the annual total energy consumption of the area, with Bavaria, a region with high consumption and structural import need as well as access to large hydro storage capabilities in Alps. | Germany - Czech Republic - 1000 Austria - Germany - 3100 | Germany - Czech Republic - 1000 - Austria - Germany - 3100 - Germany - - 5000 - 10000 | Germany - Poland Germany - Czech Republic Czech Republic - Austria Internal (Germany) | 500 200 0 2000 | 350 0 250 2000
132 | HVDC Line A-North | Project 132 consists of two new HVDC cable from Emden-East to Osterath. The HVDC has a transfer capacity of 2,4 GW. The project is a grid expansion project for low-loss transmission of high power over long distances from Northern Germany to the Rhineland. Northern Germany is characterized by a large number of regenerative onshore and offshore energy sources which exceed the demand of Northern German loads. The Rhineland, however, is a high-production region with large conventional generation capacity that has to be substituted by renewable generation capacity due to the German coal phase-out. | Amprion | DE | NDP, Germany, Netzentwicklungsplan 2035 Version 2021, Project DC1, p. 389 | 2027 | 3 | False | True | New | True | 2.31.1 |  | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | 5th PCI-List: https://ec.europa.eu/energy/sites/default/files/fifth_pci_list_19_november_2021_annex.pdf The project was part of the previous TYNDP 2020, Link to the Website: https://tyndp2020-project-platform.azurewebsites.net/projectsheets/transmission/132 Further information of the project, its investments and their necessity particularly for the German Energiewende can be found in the German grid development plan (mostly in German): http://www.netzentwicklungsplan.de/en/front More detailed information can be found on the project website (in German): https://www.amprion.net/Netzausbau/Aktuelle-Projekte/A-Nord/ |  |  |  |  | Germany - Belgium Germany - The Netherlands Internal (Germany) | 600 2200 2400 | 250 600 2400
138 | Black Sea Corridor | The project consists of one 400kV double circuit OHL Cernavoda-Stalpu with in/out connection of one circuit in Gura Ialomitei, one 400 kV double circuit OHL Smardan-Gutinas in Romania and also the new 400 kV OHL Dobrujda-Burgas in Bulgaria. This project allows transfer of generation from Western cost of the Black Sea towards consumption and storage centers in Central Europe and South-Eastern Europe. | ESO, Transelectrica | BG ;RO | Planul de dezvoltare a RET perioada 2022-2031 - submitted in June 2022 for approval to the Romanian NRA , https://web.transelectrica.ro/noutati/noutati/55_2020.08.17_14-30-42.pdf | 2024 | 4 | False | True | MostlyNew | False |  | These investments are completely dependent on each other as the main enhancements in Romania and Bulgaria which remove bottlenecks and integrate RES to the network. Clustering of investments had the purpose to identify investments contributing to the increase of transfer capacity on the same corridor. Proposed Project supports market development in South East Europe which is less developed. Based on upper mentioned information it is crucial to cluster all these investment together, to fully utilize the possible benefits. | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | In the forth PCI list are included the following investments: 3.8.1 Internal line between Dobrudja and Burgas (BG) 3.8.4 Internal line between Cernavoda and Stalpu(RO) 3.8.5 Internal line between Gutinas and Smardan(RO) http://www.transelectrica.ro/web/tel/proiecte-de-interes-comun Romanian National Development Plan (only in Romanian):https://www.transelectrica.ro/web/tel/plan-perspectiva |  |  |  |  | Bulgaria - Romania | 600 | 600
142 | CSE4 | The project concerns the construction of a new AC 400kV interconnection between Bulgaria and Greece and new AC 400kV overhead lines at the south part of Bulgaria. This project will increase cross border transfer capacity between Bulgaria and Greece | ESO, Admie | BG ;GR | https://www.eso.bg/fileObj.php?oid=3505, Bulgaria,NDP2022, page 22, NDP2022-2031, Greece, 2021, pr. No 17.8, page 106, 152, 168-170, https://www.admie.gr/sites/default/files/users/dssas/DPA%202022-2031/%CE%94%CE%A0%CE%91%202022-2031.pdf | 2022 | 4 | True | False | New | False |  | The results of market calculations in the CSE Region in the main direction of flows “North to South” have shown the need to increase transfer capacity by 500MW at the BG-GR border in the past TYNDPs. Further to market results, grid studies were performed in order to define the necessary projects to address this need. The construction of a new interconnection line between Bulgaria and Greece (main investment) along with several new internal 400kV lines to avoid bottlenecks in Bulgaria were necessary in order to accommodate flows in CSE Region and achieve the 500MW increase at the BG-GR border. These new internal 400kV lines (investments included in the project) in Bulgaria are located in the south part of the country and reinforce the 400 kV network between the connection point of the new BG-GR interconnection and the rest of the network in Bulgaria. This project will increase cross border transfer capacity between Bulgaria and Greece and achieve strengthening of the 400kV network in the south Balkan peninsula. All investments of the project are either in permitting or under construction. From the past to present the project has been integrated into the national Ten-Year Network Development Plans (TYNDP) of Greece and Bulgaria as well as in the last four ENTSO-E TYNDPs (2012, 2014, 2016 and 2018) and it has been included in the 1st, 2nd 3rd and 4th PCI lists. | TYNDP 2012 ;TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | "Project website ESO (http://projects.eso.bg/maritsa-east-nea-santa/?en#PROJECT%20OF%20COMMON%20INTEREST) - Project website IPTO (http://www.admie.gr/en/transmission-system/system-development/projects-of-common-interest/project/article/2194/) Project 142 includes a new interconnection between Bulgaria and Greece and relevant reinforcements in the 400kV network at the south part of Bulgaria. The later are necessary in order to alleviate congestions in the area of south Bulgaria that are restricting power exchanges through the new interconnector." | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The project contributes in reducing price differentials indicated in the south part of the region by providing access to more competitive generation sources located in the northeast part. The project will allow further RES integration in northeast part of Greece and in northeast and south Bulgaria. |  |  | Bulgaria - Greece | 930 | 600
144 | Mid Continental East corridor | The project consists of one double circuit 400 kV interconnection line between Serbia and Romania and reinforcement of the network along the western border in Romania: one new simple circuit 400 kV line from Portile de Fier to Resita and upgrade from 220 kV double circuit to 400 kV double circuit of the axis between Resita and Arad, including upgrade to 400 kV of three substations along this path: Resita, Timisoara, Sacalaz. The main aim of this project is increasing the transmission capacity along the East-West corridor in the South-Eastern and Central Europe, simultaneously contributing to the market integration in the region of interest and enhancing the integration of large renewable sources in the Banat region, located in the close proximity of the Serbia-Romania and Hungary-Romania borders. Along with that, the commissioning of the project will strongly improve the security of supply in the mentioned area, thus fulfilling one of the primary postulates of the modern transmission systems' reliable operation. | EMS, Transelectrica | RO ;RS | Planul de dezvoltare a RET perioada 2022-2031 - submitted in June 2022 for approval to the Romanian NRA , https://web.transelectrica.ro/noutati/noutati/55_2020.08.17_14-30-42.pdf; Plan razvoja prenosnog sistema Republike Srbije za period 2019 - 2028, Serbia, 2019-2027, page 115 | 2029 | 3 | True | False | MostlyNew | True | 3.22 | This Project aims to enhance the transmission capacity along the East-West corridor in the South-Eastern and Central Europe. The investments are complementing each other as the main enhancements in Romania which remove bottlenecks and integrate RES to the network. Clustering of investments had the purpose to identify investments contributing to the increase of transfer capacity on the same corridor. Based on upper mentioned information it is crucial to cluster all these investments together, to utilize the possible benefits. | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | On the fourth PCI list are included the following investments: PCI 3.22.1 Interconnection between Resita (RO) and Pancevo (RS) PCI 3.22.2 Internal line between Portile de Fier and Resita (RO) PCI 3.22.3 Internal line between Resita and Timisoara/Sacalaz (RO) PCI 3.22.4 Internal line between Arad and Timisoara/Sacalaz (RO) http://www.transelectrica.ro/web/tel/proiecte-de-interes-comun Romanian National development Plan (only in Romanian): https://www.transelectrica.ro/web/tel/plan-perspectiva | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The increase of transfer capacity at the boundary between Romania and Serbia will support the large scale integration of RES (the curtailed energy will decrease). | Romania - Serbia - 844 | Serbia - Romania - 1524 - | Hungary - Romania Romania - Serbia | 617 844 | 335 600
150 | Italy-Slovenia | The project is about a new HVDC link between Salgareda (Italy) and Divaca/Bericevo (Slovenia) which will strengthen the connection between Slovenia and Italy. On Italian side the project is under authorization since 2012 and the permitting process is now closed to the conclusion. On Slovenian side the project is under consideration. ELES has performed a study based on TYNDP 2020 from the perspective of the Slovenian System, which determined that most of the benefits start arising from 2040 onwards, leading to the conclusion that its implementation should be planned accordingly. Terna and ELES will continue evaluating options for increasing NTC between Slovenia and Italy in the new TYNDP scenarios considering various solutions: • reinforcement of existing grid (PSTs, upgrade of existing lines) with 400 MW Delta NTC target • HVDC link with rated power up to 1000 MW | Eles, Terna | IT ;SI | Avanzamento Piani di Sviluppo precedenti 2015/Pag.190, Italy | 2042 | 1 | True | False | New | False |  | A better vision of the project will provided in next TYNDP 2024 in line with information included in IT NDP 2023. | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | False | PCI website: https://ec.europa.eu/energy/sites/ener/files/documents/pci_3_21_en.pdf Slovenian NDP (only in slovenian): http://www.eles.si/za-poslovne-uporabnike/razvoj-in-uporaba-prenosnega-omrezja/strategija-razvoja-elektroenergetskega-sistema-rs.aspx Italian Development Plan: http://www.terna.it/it-it/sistemaelettrico/pianodisviluppodellarete/pianidisviluppo.aspx | Infrastructure to reduce price differentials between EU and/or non-EU countries Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project contributes to lowering the price differentials between Italian and Slovenia market zones This project will contribute to overcome flexibility/stability problems due to scarcely meshed grid This project will improve the integration of Italian RES generation | Italy - Slovenia - 125 | Italy - Slovenia - 125 - Italy - - 1000 - 5000 | Italy - Slovenia | 1000 | 1000
153 | France-Alderney-Britain | France-Alderney-Britain (FAB) is a new HVDC subsea interconnector between Exeter (UK) and Menuel (France) with 1,25 GW capacity. Motivation for the project : The project has as its main objectives to increase the interconnection capacity between France and Great Britain, to answer the market needs, to integrate additional RES generation and to improve security of supply. | FABLINK Limited, Rte | FR ;GB | NDP1, UK, n°153, 2017 , page 21 - NDP2, France, SDDR (Schéma Décennal de Développement du Réseau -Ten Year Network Development Scheme), France, 2019, project n°127, page 442, https://www.rte-france.com/fr/article/evolution-du-reseau-electrique-francais-l-horizon-2035 | 2030 | 3 | True | False | New | False |  |  | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | False | More information related to the project can be found on internet platforms : http://www.fablink.net and https://www.rte-france.com/fr/projet/interconnexion-france-aurigny-grande-bretagne-fab. The project is also part of both System Operator National Development Plans. In addition, FAB project has been confirmed on 31st of October 2019 as Project of Common Interest 1.7.1 in the priority corridor Northern Seas Offshore Grid (NSOG). | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. | FAB will provide cross border capacity facilitating further access between French and GB markets thereby converging GB and French prices. The GB and French generation mixes are fundamentally different and both are forecast to undergo significant change over the assessment period. FAB will provide further capacity between these two markets enhancing security of supply and reducing the risk of power failures. With increasing levels of RES forecast for both France and GB, FAB will support the integration and provide these generators access to wider markets thereby reducing the chance of curtailing these carbonized sources of power. Entsoe has identified a need for an additional 4800 MW of interco FR-UK over the 4000 MW currently. FAB contributes to this objective and to the reduction of price differentials and to reach the 15% interconnection target for 2030. | France - UK - 4800 | France - UK - 4800 - France - - <1000 | France - United Kingdom | 1400 | 1400
170 | Baltic States Synchronization with Continental Europe | Goal of the project is to prepare Baltic states electrical networks for synchronous operation with Continental Europe. Synchronization of the Baltic States with the CESA will take place by modification of the existing connection between Lithuania and Poland (LitPol Link), and a new HVDC submarine cable (Harmony Link). Internal electricity transmission grids of the Baltic States and Poland will also be strengthened, the system will be ready for disconnection from the IPS / UPS system and for independent frequency control, and synchronous condensers will be installed. As part of the project, a new HVDC connection will be established between LT-PL (investment No. 1034) allowing for a commercial exchange of the Baltic States with Continental Europe in the amount of 700 MW. | AST, Elering, Litgrid AB, Polskie Sieci Elektroenergetyczne S.A. | EE ;LT ;LV ;PL | Lithuania: "Development plan of the electric power system and transmission grid. 2021-2030" (https://www.litgrid.eu/uploads/files/dir580/dir29/dir1/10_0.php), June 2021, pages 22, 40-43. Estonia: NDP (https://elering.ee/sites/default/files/public/VKA2020.pdf) pages 41-42; Latvia: NDP "The Power Transmission System Development Plan 2022-2031", approved by resolution of the Public Utilities Commission Council of 21 October 2020, Annex 3. Poland: "Development Plan for meeting the current and future electricity demand for 2021-2030", Poland, Year 2020, Project II.88, II.26, II.27, II.28, II.29, II.34, II.35, II.36, Page 42, https://www.pse.pl/documents/31287/84e7121a-e0c0-4dee-ab2c-61bba30f4646?safeargs=646f776e6c6f61643d74727565. | 2025 | 1 | True | False | MostlyNew | True | 4.8 | After desynchronisation of Baltic States from Russia and Belarus electricity networks, electricity system in Baltic States should be ready for reliable and secure operation having one synchronous double-circuit 400 kV AC line on border with Poland. This goal could be achievable only when eliminating all negative contingency (n-1) factors and eliminating internal bottlenecks in Baltics and Poland. All investments in this project serves one or another goal from above. | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | https://www.litgrid.eu/index.php/synchronisation/synchronisation/31363 https://www.ast.lv/en/projects/synchronisation-europe | Infrastructure to allow by 2025 for the synchronisation of the Baltic States with the rest of the EU network Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. | Investments are essential part to be able to synchronize Baltics with Continental Europe synchronous area. Several synchronous compensators will be added in the system which will significantly improve RoCof. Without additional measures RoCof would increase over acceptable level. HVDC Harmony Link will increase NTC between Lithuania and Poland. HVDC Harmony Link will increase cross-border capacity between Lithuania and Poland. | Lithuania - Poland - 700 | Latvia - - <1000 Estonia - - <1000 Lithuania - Poland - 700 - Poland - - <1000602 | Lithuania - Poland | 500 | 1000
174 | Greenconnector | Greenconnector is an HVDC interconnector project between Italy and Switzerland for power transport using DC cables rather than overhead lines. The route length is about 165 km. The design power is 1000 MW (1200 MW in overload condition), while the DC voltage is +/- 400 kV DC. Two cables will be installed, working with a bipolar scheme. Great part of the cables route will exploit a section of an existing oil pipeline, no longer in service since January 1997. This pipeline crosses the Italian and Switzerland border at Splügenpass and is running close by the two end stations of the Greenconnector project (Bonaduz in Graubunden Canton and Verderio, Lecco). The cables will be pulled inside the pipeline itself, reducing the amount of civil works required before and after cable laying and therefore limiting even temporary environmental impact. For about 47 km the cables will run across the Como lake. The selected technology and voltage level make it possible to build a very efficient interconnector with very low losses. | Worldenergy SA | CH ;IT | Terna Piano di Sviluppo 2021, Italy, chap. 1.3.3, page 38 and chap. 4.3.3.2.2.3, page 262, url: https://download.terna.it/terna/Piano_Sviluppo_2021_8d94126f94dc233.pdf | 2026 | 3 | True | False | New | True | 2.14 |  | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | True | Project website: www.greenconnector.it The Greenconnector project has been selected by the Renewables Grid Initiative "Good Practice of the Year" award jury as one of the favourite practices in the "Environmental Protection" category. As a relevant and applaudable practice, Greenconnector appears in the award brochure that has been presented at the award ceremony at the European Energy Infrastructure Forum in Copenhagen on June 1, 2017. | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Greenconnector will increase the overall transmission capacity at the Northern Italian border. The total increase in power exchange will cause, as a result, the displacement of less efficient power plants and the selection of the optimum generation technology, thus resulting in overall lower prices to the consumers. Greenconnector will provide a significant contribution to the targets described in the need. In particular, the 15% interconnection target by 2030 is not achieved at the Italian northern border, as this ratio is currently below 10%. Greenconnector as a flexible and fully controllable HVDC VSC interconnector can be operated to provide international balancing flexibility and sharing of reserves, in addition to other local services (black start, voltage regulation) Greenconnector will improve the exchange of RES between Italy and Switzerland / Central Europe. The overall effect will be a better integration of RES along the North-South axis. | Italy - Switzerland - 200 | Italy - Switzerland - 2200 - Italy - - 1000 - 5000 Switzerland - - <1000 | Switzerland - Italy | 1000 | 1000
176 | Hansa PowerBridge I | New HVDC interconnector between Sweden (SE4) and Germany (50 Hertz, Continental) aiming to enhance the integration of the Nordic and the continental power market. Moreover the interconnector facilitates RES integration and increases the system adequacy in both systems. | 50Hertz, Svenska kraftnät | DE ;SE | German NEP2035, version 2021, 2nd draft, Germany, 2021, project 50HzT-P221, p. 272-274; System Development Plan 2020-2029, Sweden, 2019, p.81 | 2026 | 3 | True | False | New | False |  |  | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | The last version of the German national development plan with the project No. 176 was published in 2021 und is available under the following link: https://www.netzentwicklungsplan.de/de/netzentwicklungsplaene/netzentwicklungsplan-2035-2021 Svenska kraftnät has published a national development plan in 2019. The purpose of the plan is to be an investment plan for the following ten years, 2020-2029. The investment plan presents a detailed look of the projects Svenska kraftnät intends to realize under the stated time period. The plan is available in Swedish through the following link: https://www.svk.se/siteassets/om-oss/rapporter/2019/systemutvecklingsplan2020-2029.pdf (Swedish) | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The main driver is market integration of the Nordic hydro/nuclear/RES dominated system with the German thermal/RES based system. The infrastructure will reduce price differentials between EU countries. The system adequacy is enhanced in Germany which will increase the import potential in period of low wind and solar generation. Also the system adequacy in southern Sweden is enhanced since it given more import capacity in a future with less available nuclear generation capacity. Increase of RES in both countries leads to higher need for trade with high surplus during high wind power production. Flows are to be balanced with southbound flow during peak hours and when hydro inflow in Sweden are high and northbound in periods of high German RES generation by night | Germany - Sweden - 1400 | Germany - Sweden - 2900 - Germany - - 5000 -10000 | Germany - Sweden | 700 | 700
183 | DKW-DE, Westcoast | New 400 kV line from Endrup (DK) to Klixbüll (DE), increasing the transfer capacity at the West Coast between these countries. The project is labelled by the EC as project of common interest (PCI 1.3.1). | Energinet, TenneT DE | DE ;DK | German NDP 2035 v2021 p. 349 ff ; Denmark: RUS-plan 2018 p. 24 and 37 | 2023 | 3 | True | False | New | False |  |  | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | www.klixbuell-endrup.eu | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | contributes to reduction of price spread by 2040 facilitates exchange of RES and reserves increases system size, thus facilitates sharing of ancillary service high RES increase expected on both sides of the border - further connection to low correlated RES area (GB) via project in vicinity. |  |  | Germany - Denmark | 1000 | 1000
186 | East of Austria | To allow the grid integration of the planned renewable energy generation (mainly wind power) in the north-eastern part of Austria ("Weinviertel") the transmission grid infrastructure (currently a rather weak 220kV line) has to be enforced and new substation for the connection needs to be erected. | Austrian Power Grid | AT | APG Netzentwicklungsplan 2021, AT, 2021, 11-8, 45, https://www.apg.at/de/Stromnetz/Netzentwicklung | 2022 | 4 | False | True | New | False |  |  | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | Project homepage: https://www.apg.at/en/projekte/ersatzneubau-apg-weinviertelleitung National development plan: https://www.apg.at/en/Stromnetz/Netzentwicklung | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) | Projects improves connection of wind generation with sufficient capacity to the transmission system and enables future RES development. Projects improves connection of wind generation with sufficient capacity to the transmission system and enables future RES development. The project provides the opportunity to integrate additional electrolysers (P2G) in the region. |  |  | Internal (Austria) | 2000 | 2000
187 | St. Peter (AT) - Pleinting (DE) | Increase of the cross border transmission capacity by erecting a new 380kV line between St. Peter (Austria) and Pleinting (Germany). This leads to an improved connection of the very high amount of RES in Germany and the pump storages in the Austrian Alps. | Austrian Power Grid, TenneT DE | AT ;DE | DE:NEP2035 v2021 p. 468 ff; APG Netzentwicklungsplan 2021, AT, 2021, 11-7, 58, https://www.apg.at/de/Stromnetz/Netzentwicklung | 2030 | 3 | True | False | New | False |  |  | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | True | This project is highly connected to and partly based on TYNDP 2016 Project 47/Investment 212. German grid development plan: http://www.netzentwicklungsplan.de/content/der-netzentwicklungsplan-0 Austrian National development plan: http://www.apg.at/en/netz/netzausbau/Netzentwicklungsplan Austrian Project homepage Austria: https://www.apg.at/en/projekte/380-kv-deutschland-leitung | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | helps to reach the target in Germany high RES generation connected to pump storage high RES generation connected to pump storage | Austria - Germany - 3100 | Austria - Germany - 3100 - Germany - - 5000 - 10000 Austria - - <1000 | Austria - Germany | 1500 | 1500
190 | NorthConnect | A 665 km long subsea interconnector between Norway and Scotland is planned to be realised in 2024. The interconnector is planned to be a 1400 MW HVDC subsea interconnector between western Norway (Simadalen) and eastern Scotland (Peterhead), UK. | NorthConnect | GB ;NO | (1) Nordic Grid Development Plan 2019 https://www.statnett.no/contentassets/61e33bec85804310a0feef41387da2c0/nordic-grid-development-plan-2019-for-web.pdf (2) National Grid NOA (Network Options Assessment Plan 2018/2019) https://www.nationalgrideso.com/document/137321/download (3) National Grid ETYS (Electricity Ten Year Statement) nov 2018 https://www.nationalgrideso.com/document/133836/download | 2027 | 1 | True | False | New | False |  | NA | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | https://northconnect.co.uk/ | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Main driver is to assist to security of supply in each country by balancing out volatile weather dependent energy production in each country. In Scotland system adequacy has challenges in period of low wind, while Norway has challenges in period of limited precipations. The project provides significant ramp up capacity The project is targeting the sale of ancillery services for both countries, in particular as the Norwegian hydro-power based poweer system is especially strong and flexible at the landing point of Sima. By providing market outlet in Northen Scotland and Western Norway for further wind developments or new investments of hydropower in Norway, the project enable efficient grid connection of high volumes of RES. The project alleviate grid congestion issues in each country.and contribute to a significant reduction in curtailment of renewable energy. | Norway - UK - 1400 | Norway - UK - 1400 - | United Kingdom - Norway | 1400 | 1400
200 | CZ Northwest-South corridor | A corridor of internal 400 kV overhead lines inside the Czech Republic connecting new 420 kV substations between Vernerov, Vitkov and existing substation Prestice (OHL Prestice - Vitkov was already commissioned in 2021) in the northwest-south direction. The project consists building of two 400 kV overhead lines involving changing a 220 kV double-circuit lines to 400 kV double-circuit lines with a capacity of 2 x 2445 A each between Vernerov and Vitkov and Vitkov and Prestice. Part of the project is also a construction of a new 420 kV substation Vitkov (already commissioned in 2020) and upgrading and extension of the existing 420 kV substation Kocin (phase 1 was already commissioned). | CEPS | CZ | Ten-year investment plan for the development of the TS 2021 – 2030, CZ, 2021, V487/488–Line Doubling, 87 pg., https://www.ceps.cz/en/transmission-system-development | 2024 | 3 | False | True | MostlyNew | True | 3.11.1 and 3.11.2 | Project 200 that contains investment item 308 (item 309 was already commissioned) altogether with project 35 that contains investment items 313 and 315 forms a geographically continuous (uninterrupted) network corridor from a new 420 kV substation Vernerov (already commissioned at the end of 2017), through a new 420 kV substation Vitkov (which is also already commissioned at the end of 2020), existing 420 kV substation Prestice, existing 420 kV substation Kocin and ending up to the existing substation 420 kV Mirovka. It is actually what is referred as a “convoy lines” or "sequential projects" with all 4 involved 400 kV overhead lines (investment 308 (Vernerov-Vitkov), 309 (Vitkov-Prestice), 315 (Prestice-Kocin) and 313 (Kocin-Mirovka)) connected in series forming a corridor from the northern-western part of the Czech grid related to the DE-CZ border into the south and eastern direction towards the CZ-SK and CZ-AT borders. | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | Information about Czech development plan and PCI projects can be found on the following links below on the CEPS website: https://www.ceps.cz/en/transmission-system-development https://www.ceps.cz/en/pci-projects-of-common-interest | Infrastructure to reduce price differentials between EU and/or non-EU countries Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project helps to decrease the curtailed energy in Germany due to extra market transfers (increase of NTC) on the profile DE - CZ which lead to reduction of marginal price. The project contains the upgrade of existing 220 kV lines to 400 kV lines which will reduce infrastructure vulnerability and therefore ensure reliable and secure operation of the grid. This project besides the increase of NTC also consists of reinforcement of internal lines and therefore facilitates the future need for cross-border flows. The project is aiming at facilitation of the power flows from the RES generation in the northern part of Europe and western part of CZ therefore promotes RES integration. |  |  | Czechia - Germany | 500 | 500
210 | Würmlach (AT) - Somplago (IT) interconnection | Somplago - Würmlach interconnection is a cross-border electrical line promoted by Alpe Adria Energia Srl. The project concerns a 220kV a.c. merchant line, about 300 MW thermal capacity from Somplago substation to new Würmlach substation, including Phase Shifter Transformer located in Austria. | Alpe Adria Energia Srl | AT ;IT |  | 2026 | 3 | True | False | New | False |  |  | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | Web site: https://corporate.enel.it/en/stories/a/2017/01/alpe-adria-energia | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The Project will increase the cross-border capacity between the interconnected Countries and will allow market exchanges which lead to a minimising price differentials of the Italian border also in line with the interconnection target recommendations (Nov 2017) by EC Expert Group. The project will enhance the adequacy of the interconnected systems in the mid/long-term scenarios with a different generation mix . In particular, it improves the share of the renewable energy sources and new flexible thermal generation in the electricity systems involved by the line. The Project contributes to increase the Italian cross-border capacity in the medium-long term objectives (2030) as also reported in the Italian Implementation Plan for the requirements set in article 20 of Regulation 2019/943 of 5th June 2019 on the Internal Electricity Market (IEM). This cross border project allows higher flows in the meshed AC-grid and consequentially it allows better integration of RES in the interconnected Countries. | Austria - Italy - 500 | Austria - Italy - 1000 - Italy - - 1000 - 5000 Austria - - <1000 | Austria - Italy | 150 | 150
219 | EuroAsia Interconnector | The EuroAsia Interconnector PCI 3.10 is a multi-terminal VSC-HVDC scheme which will connect the transmission networks of Greece (Crete), Cyprus and Israel, and will comprise two converter stations with sea-electrodes, interconnected by HVDC cable systems. The initial development will allow the bidirectional transfer of 1000 MW. At full deployment, it will allow the transfer of 2000 MW. Its total offshore length is 1208 km (310 km CY-IL, 898 km CY–Crete) while its onshore length is 25 km. The cables will be laid at a max. water depth of 2200 m between IL and CY and 3000 m between CY and CR. The EuroAsia Interconnector is a European Project of Common Interest (PCI) since 2013 listed in the ‘NSI East Electricity’ priority corridor. It is defined as a cluster PCI 3.10 consisting of the following PCIs: • PCI 3.10.1 – Interconnection Hadera (IL) - Kofinou (CY) • PCI 3.10.2 – Interconnection Kofinou (CY) - Korakia, Crete (EL) | EuroAsia Interconnector | CY ;GR ;IL | Yes, Title of the document: “ΔΕΚΑΕΤΕΣ ΠΡΟΓΡΑΜΜΑ ΑΝΑΠΤΥΞΗΣ ΣΥΣΤΗΜΑΤΟΣ ΜΕΤΑΦΟΡΑΣ 2022-2031” Country: Greece Year: 2021 Page number: 171 TSO: IPTO url: https://www.admie.gr/sites/default/files/users/dssas/DPA%202022-2031/%CE%94%CE%A0%CE%91%202022-2031.pdf. Title of the document: “ΔΕΚΑΕΤΕΣ ΠΡΟΓΡΑΜΜΑ ΑΝΑΠΤΥΞΗΣ ΣΥΣΤΗΜΑΤΟΣ ΜΕΤΑΦΟΡΑΣ 2021-2030” Country: Cyprus Year: 2021 Page number: 9 TSO: TSOC url: https://tsoc.org.cy/files/electrical-system/tydplan/%CE%94%CE%A0%CE%91%CE%A3%CE%9C%202021-2030%20web.pdf | 2026 | 3 | True | False | New | True | 3.10.1 and 3.10.2 | The projects have been clustered for more efficient procedures regarding licencing since it involves three countries | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | https://euroasia-interconnector.com/ | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) | The project will connect Cyprus to the continental electricity network allowing for energy imports / exports and trading, ensuring security of supply and rendering the wholesale electricity prices lower and more competitive The project will, end the energy isolation of Cyprus as the last isolated EU member, contribute to the 15% interconnection target of EU members, boost competition, reduce the cost of energy and ensure security of energy supply for the involved countries and the EU The Interconnector can offer the means to reach the RES integration goals since it will enable the transmission of RES-generated electricity across the countries involved and avoid RES curtailment. Furthermore, the Interconnector can reduce the phenomenon of curtailed RES which persists at times in the countries involved VSC technology is characterised by a full range Reactive power management control also offers the possibility of black start capability and therefore the EuroAsia Interconnector offers alternative ways of speeding up the restoration process in a country availing of the power supply through the VSC station | Cyprus - Greece (Crete) - 1000 Cyprus - Israel - 1000 | Cyprus - Greece (Crete) - 1000 - Cyprus - Israel - 1000 - Cyprus - - <1000 | Cyprus - Greece Cyprus - Israel | 1000 1000 | 1000 1000
225 | 2nd interconnector Belgium - Germany | This project considers the possibility of a second ~1GW HVDC interconnection between Belgium and Germany at the earliest by 2038 (indicative timing). The timing as well as location, routing, capacity are subject to further studies. Project motivation: Preliminary studies have indicated potential for further regional welfare increase by further increasing the interconnection capacity between Belgium and Germany. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials. This interconnector project is designed as a HVDC-link. The full controllability of the HVDC link facilitates the balancing of active and reactive power in the Belgian and German grid. Belgium and Germany face decreasing figures of installed conventionals due to bad market conditions. The interconnector contributes to meet adecacy not only in both countries but also in the entire CWE-region. Due to the future RES increase in whole CWE the RES spillage will rise significantly especially beyond 2030. This interconnector project allows a better integration of RES in the entire region. | Amprion, Elia | BE ;DE | NDP1, Belgium, 2020-2030, §4.2.3.4; NDP2, Germany, Netzentwicklungsplan 2035 Version 2021, Project 313, p. 559 | 2038 | 1 | True | False | New | False |  |  | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | False | More information about the project can be found following this link: - National Development Plan: https://www.elia.be/-/media/project/elia/elia-site/infra-and-projects/investment-plans/federal-development-plan-2020-2030/nl/20190516_federaal-ontwikkelingsplan_nl.pdf?la=en The project was part of the previous TYNDP 2020, Link to the Website: https://tyndp2020-project-platform.azurewebsites.net/projectsheets/transmission/225 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between the Belgian and German bidding zones. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials Belgium and Germany face decreasing figures of installed conventionals due to bad market conditions. The interconnector contributes to meet adequacy not only in both countries but also in the entire CWE-region This interconnector project between Belgium and Germany is designed as a HVDC-link. The full controllability of the HVDC link facilitates the balancing of active and reactive power in the Belgian and German grid Due to the future RES increase in whole CWE the RES spillage will rise significantly especially beyond 2030. This interconnector project allows a better integration of RES in the entire region | Belgium - Luxemburg - 500 Germany - Luxemburg - 400 | Belgium - Luxemburg - 500 - Germany - luxemburg - 400 - Belgium - - <1000 Germany - - 5000 - 10000 | Belgium - Germany | 1000 | 1000
227 | Transbalkan Corridor | This project contains seven investments, with the new corridor spanning from Central (SS Kragujevac 2 and SS Kraljevo 3) and Western Serbia (SS Obrenovac and SS Bajina Basta) all the way to SS Visegrad in Bosnia and Herzegovina and SS Lastva (across SS Pljevlja 2) in Montenegro. As can be seen from the brief list of the investments, the project aims to increase both the transmission capacity within Serbian transmission system and the transfer capacities on the borders between the mentioned countries. Thus, it is expected that it will largely facilitate the energy exchange between the north-east and south-west parts of Europe, setting a foundation for the enhanced market integration and leveling of the marginal energy costs and guaranteeing the security of supply throughout the region. This project is tightly connected to the project 28 (Italy - Montenegro) and the project 342 (Central Balkan Corridor). | EMS, NOS-BIH, CGES | BA ;IT ;ME ;RS | Plan razvoja prenosnog sistema Republike Srbije za period 2020 - 2029 (JSC EMS Development Plan 2020-2029), page 120, available at: http://www.ems.rs/media/uploads/Plan-razvoja-prenosnog-sistema-Republike-Srbije-2020-2029.pdf; Plan razvoja prenosnog sistema 2020-2029 (CGES Development Plan 2020-2029), page 150, available at: https://www.cges.me/regulativa/razvoj-sistema; Dugorocni plan razvoja prenosnog sistema 2021-2030 (NOS BiH Development Plan 2021-2030), page 46, avalable at: https://www.nosbih.ba/files/2021/03/20210311-lat-Dugorocni-plan-razvoja-prenosne-mreze-2021-2030-Knjiga-1.pdf. | 2026 | 3 | True | False | MostlyNew | False |  | These investments will form new HV AC and DC corridor from Serbia, through Montenegro to Italy (with project 28), enhancing energy exchange and further market integration in SEE region. | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | http://ems.rs/media/uploads/Plan_razvoja_prenosnog_sistema_2.pdf | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. | This project significantly aids the energy market integration, set as one of the top priorities of the European grid development, and, as such, massively helps the process of equalizing the marginal energy prices in the EU and non-EU countries, which is particularly relevant for the CSE region. As the power lines in the Western Serbia are rather old and should be decommissioned due to their age, this project will provide an alternative for them, resolving, among other benefits, the issues related to security of supply, becoming increasingly important with the growth of load in this region. Even though the impact that this project may have on the connection of RES, the Drina river, located near the foreseen paths of OHLs included in the project, offers significant additional potential for energy generation in hydro capacities, thus amplifying the importance of Transbalkan corridor for this system need. This project will contribute to the parameters of system stability in two ways - by increasing the NTC values and enabling the larger cross-border energy trades, and by allowing the connection of new HPSPP Bistrica to the grid, foreseen as the large flexibility source in this region. | Montenegro - Serbia - 840 Bosnia-Herzegovina - Serbia - 2310 | Montenegro - Serbia - 840 - Bosnia-Herzegovina - Serbia - 1200 - | Montenegro - Serbia Bosnia and Herzegovina - Serbia | 80 1130 | 430 710 | Transbalkan Corridor which connects non-EU countries is tightly connected to the project 28 which connects EU and non-EU countries (Italy - Montenegro) and both of them will directly enable market exchanges and power flows between EU countries via non-EU countries (from Hungary, Romania and Bulgaria via Serbia and Montenegro towards Italy and vice versa). What should be stated here is that the Transbalkan corridor exists in the reference grid used for project assessment, unlike the project 28. This means that the project 227 was assessed without taking the project 28 into account, whereas the project 28 was assessed with project 227 in operation, justifying the high difference in the obtained SEW values between these projects. Nonetheless, this means that the project 227 should also be viewed through the perspective of the high benefits of the project 28, rather than solely through the prism of its own benefits. Transbalkan corridor became even more important after the decision that new hydro pump storage power plant Bistrica (installed capacity 700 MW) will be built and connected to the cross-border part of Transbalkan corridor. Hydro pump storage power plant Bistrica will highly contribute to RES integration in South Eastern Europe and improve the system stability and flexibility, as well as the system balancing under the conditions dictated by the new generation mix and the green transition. The mentioned impact on energy exchanges in the region especially comes as benefit after the commissioning of other projects that will increase NTCs between Serbia and neighboring countries (Pannonian Corridor, North CSE Corridor, Central Balkan Corridor). The project 227 is direct precondition for project 342 (Central Balkan Corridor).
228 | Muhlbach - Eichstetten | Reinforcement of the existing 400kV OHL and deployment of a second 400kV circuit at existing dou-ble circuit OHL Muhlbach - Eichstetten, instead of the currently operated circuit Eichstetten - Vogelgrun (currently operated with 225kV). The project includes also a transformer in Sierentz substation to balance flows between 225kV and 400kV grid in the area. Motivation for the project: Germany and the Continental Central South-Region is characterised by a significant increase in RES generation. The grid has to be developed in order to support these new exchange possibilities, facilitating the access to the most economic energy mix, while minimising grid congestions. High flows in both directions West-East and North-South are expected. By increasing of interconnection capacity, the project strengthens the European electricity market and contributes to the security of supply. | Rte, TransnetBW | DE ;FR | German NDP: Netzentwicklungsplan Strom 2035 Version 2021, Germany, Project No.176, p.507; https://www.netzentwicklungsplan.de/sites/default/files/paragraphs-files/NEP_2035_V2021_2_Entwurf_Teil2.pdf; French NDP: SDDR (Schéma Décennal de Développement du Réseau -Ten Year Network Develop-ment Scheme), 2019, France, project No. 880, page 442, https://www.rte-france.com/en/analyses-trends-and-perspectives/ten-year-network-development-plan#Documents | 2026 | 2 | True | False | Upgrade | False |  |  | TYNDP 2014 ;TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | German National Development Plan: NEP 2035 Version 2021: https://www.netzentwicklungsplan.de/sites/default/files/paragraphs-files/NEP_2035_V2021_2_Entwurf_Teil2.pdf French National Development Plan: SDDR (Schéma Décennal de Développement du Réseau -Ten Year Network Develop-ment Scheme), 2019, France, project No. 880, page 442, https://www.rte-france.com/en/analyses-trends-and-perspectives/ten-year-network-development-plan#Documents Bundesbedarfsplan 2021: https://www.netzausbau.de/Vorhaben/ansicht/de.html?cms_nummer=72&cms_gruppe=bbplg http://www.gesetze-im-internet.de/bbplg/BJNR254310013BJNE000605377.html Project specific websites: TransnetBW: https://www.transnetbw.de/de/netzentwicklung/projekte/eichstetten-bundesgrenze-frankreich/projektueberblick | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Reduction of the loop flows occurrence in the borders between CZ-DE, DE-PL, DE-NL-BE-LU-FR-DE Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Although this is not the main driver for this project, increase the interconnectivity between the German and French bidding zone give the possibility of higher market exchanges between these two bidding zones leading to a higher price convergence in more hours of the year. France and Germany face decreasing figures of installed conventionals due to reduction or phaseout of nuclear and bad market conditions for other conventionals. The interconnector contributes to meet adequacy not only in both countries but also in the entire CWE region. Flows on 380kV OHL could be adjusted with both PSTs installed in Muhlbach substation rather than current 220kV interconnector. Rising figures of RES capacities especially in Germany lead to increasing RES-curtailment in the coming decades. This interconnector project allows a higher export in hours of high RES infeed particularly in Western Germany. |  |  | Germany - France | 300 | 300
230 | GerPol Power Bridge I | The reinforcements in the Polish transmission network in western part of the country near Polish/German border. Construction new AC 2x400 kV lines Mikułowa - Świebodzice, Krajnik - Baczyna, Baczyna - Plewiska and new substation 400/110 kV Baczyna. | Polskie Sieci Elektroenergetyczne S.A. | PL | "Development Plan for meeting the current and future electricity demand for 2021-2030", Poland, Year 2020, Project II.20, II.15, II.21, II.22, II.24, Page 42, url://www.pse.pl/documents/31287/84e7121a-e0c0-4dee-ab2c-61bba30f4646?safeargs=646f776e6c6f61643d74727565 | 2024 | 4 | False | True | New | True | 3.14 Internal reinforcements in Poland (including 3.14.2, 3.14.3, 3.14.4) | All investments in the 230 project complement each other in bringing the desired increase of Grid Transfer Capability on the Polish-German border. Vast majority of investents in this cluster connect directly to border substations and have direct impact on border flows. | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | Link to PSE S.A. Development Plan where investments of this project are included: https://www.pse.pl/documents/31287/84e7121a-e0c0-4dee-ab2c-61bba30f4646?safeargs=646f776e6c6f61643d74727565 Page: 10 and 42. The following investments from cluster are included in 4th PCI list: 3.14.2 Internal line between Krajnik and Baczyna (PL), 3.14.3 Internal line between Mikułowa and Świebodzice (PL), 3.14.4 Internal line between Baczyna and Plewiska (PL) | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Reduction of the loop flows occurrence in the borders between CZ-DE, DE-PL, DE-NL-BE-LU-FR-DE | Finalization GerPol Power Bridge I project allows to increasing cross-border capacity on Polish-German border and thus allows to exchange more energy. This project contributes to accommodate future scenarios and cross-border flows. This project contributes to reduce the occurence of unscheduled flows from DE to PL by increasing the controllability on the entire profile. |  |  | Germany - Poland | 1500 | 500
231 | Beznau - Tiengen | This project comprises the upgrade of a 220 kV crossborder line to 380 kV between the substations of Tiengen (DE) and Beznau (CH). | Amprion, Swissgrid | CH ;DE | NDP Germany, Netzentwicklungsplan 2035 Version 2021, Project P204, p.512 | 2030 | 1 | True | False | Upgrade | False |  |  | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | False | https://www.netzentwicklungsplan.de/de/projekte/projekte-nep-2035-2021 The project was part of the previous TYNDP 2020, Link to the Website: https://tyndp2020-project-platform.azurewebsites.net/projectsheets/transmission/231 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | This project contributes to lowering the price differentials between Switzerland, Germany and Austria. This project contributes to the adequacy in view of the nuclear phase-out and the development of renewables and pump hydro storage devices. This project is located in a highly meshed part of the transmission grid and therefore helps accommodate such flows. | Germany - Switzerland - 1550 | Germany - Switzerland - 1550 - Germany - - 5000 - 10000 Switzerland - - <1000 | Switzerland - Germany | 100 | 600
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Bergrheinfeld West | 4 GW HVDC connection from Northern Germany (areas of Brunsbüttel/Wilster) to Bavaria / Baden-Württemberg (areas of Großgartach/Bergrheinfeld West). North Germany is characterised by a high amount of RES, the feed-in exceeds the local load and therefore there is a high demand for transfer to the load centres in southern parts of Germany. With the further installation of additional renewable energy, the relevance of this projects increases. | TransnetBW, Tennet DE | DE | Netzentwicklungsplan Strom 2035 Version 2021 (NEP), Germany, Project No. DC3/DC4, p.393; https://www.netzentwicklungsplan.de/sites/default/files/paragraphs-files/NEP_2035_V2021_2_Entwurf_Teil2.pdf | 2026 | 3 | False | True | New | True | 2.10 |  | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | German Network Development Plan 2035 Version 2021: https://www.netzentwicklungsplan.de/sites/default/files/paragraphs-files/NEP_2035_V2021_2_Entwurf_Teil2.pdf 3rd PCI-list: https://ec.europa.eu/energy/sites/ener/files/documents/annex_to_pci_list_final_2017_en.pdf 4th PCI-List: https://ec.europa.eu/energy/sites/ener/files/c_2019_7772_1_annex.pdf Bundesbedarfsplan 2021 (BBPIG): https://www.netzausbau.de/Vorhaben/ansicht/de.html?cms_nummer=3&cms_gruppe=bbplg http://www.gesetze-im-internet.de/bbplg/BJNR254310013BJNE000605377.html Project specific websites: TransnetBW: https://www.transnetbw.de/de/netzentwicklung/projekte/suedlink/projektueberblick TenneT DE: https://www.tennet.eu/de/unser-netz/onshore-projekte-deutschland/suedlink/ | Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Reducing the redispatch leading to more flexibility and increasing the stability of the system. In critical grid situations, costly congestion management measures are taken to avoid overload of grid elements. The project will reduce the demand for re-dispatching, countertrading and curtailment of renewable energy producers by adding significant transmission capacity between the congested routes in the North-Western part of Germany. The project enables the integration of offshore and onshore wind energy by preventing potential bottlenecks in northern and southern Germany. |  |  | Germany - Denmark (West) Germany - The Netherlands Internal (Germany) | 0 2250 4000 | 1150 50 4000
239 | Fenno-Skan 1 renewal | Replacement of the existing 400 kV HVDC cable interconnection between Finland and Sweden. Fennoskan 1 will be decomissioned and a new interconnector with the capacity of 800 MW will be built between FI and SE3, resulting in a total capacity of 1600 MW between FI and SE3. Previously (in TYNDP2020) this project was planned between FI and SE2, and now it has been changed to be situated between FI and SE3. According to new studies, this location provides more market benefits. The first decision depended also on the first simulation results that showed the complexities of connection between FI and SE3. However, these complexities were not observed in the updated simulations. | Fingrid, Svenska Kraftnät | FI ;SE | Not yet included | 2040 | 1 | True | False | Upgrade | False |  |  | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | False | The concept is discussed for example in Fingrid's network vision: https://www.fingrid.fi/globalassets/dokumentit/fi/kantaverkko/kantaverkon-kehittaminen/fingrid_network_vision.pdf | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. | Adds market capacity 800 MW. Improves local power balance and mitigates risk of power failures in Sweden and Finland. Adds market capacity 800 MW. Contributes to all three interconnection targets. Improves system stability both in Sweden and Finland and Nordic synchronous area. | Finland - Sweden - 1700 | Finland - Sweden - 2500 - | Finland - Sweden | 400 | 400
243 | New 400 kV interconnection line between Serbia and Croatia | Construction of new 400 kV interconnection line Sombor (RS) - Ernestinovo (HR), expected to provide a significant asset in terms of increasing the NTC between Serbia and Croatia, hence allowing the more prominent energy flow in the East-West direction across the CSE region, improving the market integration among the beneficiary countries and further ensuring the security of supply primarily in Serbia and Croatia, but, under certain circumstances, contributing to the reliable functioning of the systems in the rest of the countries in the region as well. Alongside that, it should be mentioned that the project will have a rather positive impact related to the possibility of integration of renewable energy sources in the Backa region. | EMS, HOPS | HR ;RS | Plan razvoja prenosnog sistema Republike Srbije za period 2020 - 2029, page 157 (Serbian national TYNDP 2020-2029) - available at: http://www.ems.rs/media/uploads/Plan-razvoja-prenosnog-sistema-Republike-Srbije-2020-2029.pdf; Desetogodišnji plan razvoja prijenosne mreže 2021.-2030. s detaljnom razradom za početno trogodišnje i jednogodišnje razdoblje (Croatian NDP 2021.-2030.), Siječanj 2021., page 88, page 118 - avalable at: https://www.hops.hr/page-file/zqUlI9C05IF75yjB042gSD/92136ad3-dfa8-4674-b6aa-3c7a0d41654c/HOPS%2010G%20plan%20razvoja%20(2021%20-%202030).pdf | 2035 | 1 | True | False | New | False |  |  | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | True | http://ems.rs/media/uploads/Plan_razvoja_prenosnog_sistema_2.pdf http://www.hops.hr/page-file/zqUlI9C05IF75yjB042gSD/92136ad3-dfa8-4674-b6aa-3c7a0d41654c/HOPS%2010G%20plan%20razvoja%20(2021%20-%202030).pdf | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Since this interconnection means the increase of NTC between Croatia (EU country) and Serbia (non-EU country), it is seen as a mean of reaching the market integration goals and reducing the price differentials in the Continental Southeast Europe region. As nearly all of the scenarios foreseen for the future period predict rather high energy flow across the borders in the CSE region, each of the new interconnections in this area can be seen as an additional step towards guaranteeing the timely reaching of the set goal. In the conditions of ever higher needs for the intensive cooperation between the neighboring TSOs, every new interconnection, such as the one included in this project, can be seen as the new and valuable asset regarding the improvement of systems' flexibility and reliability of operation. According to the currently available information, the Bačka region in Northern Serbia is predicted to host several wind power plants of sustainable installed capacity (exceeding 1 GW), with new line between SS Sombor 3 and SS Ernestinovo ensuring the uninterrupted and secure evacuation of the produced energy. | Croatia - Serbia - 1600 | Croatia - Serbia - 1600 - Croatia - - <1000 | Croatia - Serbia | 600 | 600
244 | Vigy - Uchtelfangen area | An upgrade of the existing over headline between the substations Ensdorf, Uchtelfangen and Vigy is planned to increase the thermal cross-border capacity. For this reinforcement the options are either the implementation of High Temperature Low Sag (HTLS) conductors or a reconstruction of the tie-line in the existing route. To allow an optimal use of the capacity increase the installation of phase shifter transformers (PSTs) is necessary. For these measures the substations have to be adjusted accordingly. Motivation for the project : Germany and also the CCS-Region is characterised by a significant increase in RES generation. The grid has to be developed in order to support these new exchange possibilities, facilitating the access to the most economic energy mix, while minimising grid congestions. High flows in both directions West-East and North-South are expected. The project strengthens the European single market. This project increases the interconnector capacity between France and Germany and therefore also the security of supply. | Amprion, Rte | DE ;FR | NDP Germany, Netzentwicklungsplan 2035 Version 2021, Project P170 p.500 and Project P314 p.563 - NDP2; France, SDDR (Schéma Décennal de Développement du Réseau -Ten Year Network Development Scheme), 2019, project n°444, page 442, https://www.rte-france.com/en/analyses-trends-and-perspectives/ten-year-network-development-plan#Documents | 2029 | 2 | True | False | MostlyUpgrade | False |  | The two investments are for us two parts of the same project to contribute together to the increase of exchange capacity between France and Germany. For some historical reasons (different commissioning date, more clarification on the description of the project) they have been described with separate IDs . With our current overview on the project (two investments on the same elements of the grid with close commissioning dates), both RTE and Amprion consider them as two steps of the same project with no need to assess them separately. | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | True | The project was part of the previous TYNDP 2020, Link to the Website: https://tyndp2020-project-platform.azurewebsites.net/projectsheets/transmission/244 Considering the border France-Germany, the expected increase of capacity of project 244 in both direction could be fully available as soon as the two projects (228 and 244) identified on this border will be commissioned. https://www.netzentwicklungsplan.de/de/projekte/projekte-nep-2035-2021 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Reduction of the loop flows occurrence in the borders between CZ-DE, DE-PL, DE-NL-BE-LU-FR-DE Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Although this is not the main driver for this project, increasing the interconnectivity between the German and French bidding zone gives the possibility of higher market exchanges between these two bidding zones leading to a higher price convergence in more hours of the year. France and Germany face decreasing figures of installed conventionals due to reduction or phaseout of nuclear and bad market conditions for other conventionals. The interconnector contributes to meet adequacy not only in both countries but also in the entire CWE region. RES infeed in the north of Germany often bypasses via Netherlands, Belgium and France. The project allows a better limitation of these loop flows via new PSTs on the French-German border. Rising figures of RES capacities especially in Germany lead to increasing RES-curtailment in the coming decades. This interconnector project allows a higher export in hours of high RES infeed particularly in Western Germany. | France - Germany - 1500 | France - Germany - 1500 - France - - 1000 - 5000 Germany - - 5000 - 10000 | Germany - France | 1500 | 1500
247 | AQUIND Interconnector | AQUIND Interconnector is a proposed High Voltage Direct Current (HVDC) subsea and underground electric power transmission link between Great Britain (Lovedean substation, Hampshire) and France (Barnabos switching station, Seine-Maritime) with a net transmission capacity of 2,000 MW. The interconnector is designed as two parallel monopole 1000 MW circuits employing Voltage Source Converter technology. The project will be able to: • Boost competition by providing access to wider electricity markets; • Help improve security of supply by creating additional source of supply and by providing ancillary services to the respective national grids; and • Increase sustainability of energy supply by helping to integrate more renewable energy sources. The project will consist of the following elements: • One converter station on each end of the link, • The 320 kV DC subsea cable route will be approximately 182 km in length between Eastney (UK) and Pourville (France). • The British 320 kV DC terrestrial cable route will be approximately 20 km long. • The French 320 kV DC terrestrial cable route will be approximately 36 km long. • The 400 kV AC cable routes are several hundred meters in France and UK. | Aquind Limited (UK) and AQUIND SAS (France, 100% subsidiary of Aquind Limited) | FR ;GB | France – Schéma Décennal de Développement du Réseau 2019, project number 991 (page 442) - https://assets.rte-france.com/prod/public/2020-07/SDDR%202019%20Annexe%2002%20-%20Les%20projets_0.pdf. AQUIND Interconnector is also included in the latest available “Programmations pluriannuelles de l'énergie of France 2019 – 2023 2024 – 2028” (page 194) - https://www.ecologique-solidaire.gouv.fr/sites/default/files/0-PPE%20English%20Version%20With%20Annex_0.pdf. Great Britain - Future Energy Scenarios 2021, (FES Modelling Methods 2021, page 37 - https://www.nationalgrideso.com/document/199916/download). AQUIND is also included in latest available Electricity Ten Year Statement 2020, as it is part of National Grid's TEC Register (page 4 - https://www.nationalgrideso.com/document/181481/download and https://data.nationalgrideso.com/connection-registers/interconnector-register/r/interconnector_register ) | 2026 | 3 | True | False | New | False |  |  | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | False | Official Websites: English - http://aquind.co.uk/ French - http://aquind.fr/ Consultation websites: English - http://aquindconsultation.co.uk/ French - https://aquindconsultation.fr/ Investment in electricity interconnectors: immediate economic benefits and key role in the French energy transition. Example of AQUIND Interconnector. (Asterès, June 2020) - https://asteres.fr/site/wp-content/uploads/2020/06/ASTERES-AQUIND-Investir-dans-les-interconnexions-19062020.pdf AQUIND Interconnector - reducing the cost of transition to Net Zero for GB energy consumers (FTI Consulting, July 2020) - https://www.fticonsulting-emea.com/~/media/Files/emea--files/insights/reports/2020/aug/reducing-cost-transition-net-zero-gb-consumers.pdf | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Structural differences in the wholesale electricity prices between the electricity markets in GB and France clearly demonstrate the need for more capacity. By providing additional 2GW of interconnection capacity AQUIND Interconnector will reduce price differentials on a congested France - GB border. By providing additional 2GW of interconnection capacity AQUIND will contribute to reaching the objectives of the European ITEG indicators in France and GB. AQUIND Interconnector will facilitate more efficient generation dispatch in the connected markets required for cross-border balancing services AQUIND will provide an opportunity for the efficient dispatch of renewables in GB, France and across connected markets. The additional cross-border capacity provided by AQUIND offers the opportunity to export additional power, that otherwise could be curtailed, during periods of high renewable generation. | France - UK - 4800 | France - UK - 4800 - France - - 1000 - 5000 | France - United Kingdom | 2075 | 2075
250 | Merchant line Castasegna (CH) - Mese (IT) | The planned Transmission project is a merchant line on the swiss-italian border between Castasegna (CH) and Mese (IT). The planned Cable connection in 220 kV AC has a length of around 14 km, 13.5 of witch in Italy. In connection with the realisation of the project a Rationalisation of the 380 and 132 kV Grid in the region Mese (Provincia di Sondrio) is planned. The expected NTC increase is around 200-250 MW. | Repower, MERA SRL | CH ;IT | Piano di sviluppo Terna 2021. https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete. PDF, pg 262 | 2025 | 3 | True | False | New | False |  | The planned Transmission project is a merchant line on the swiss-italian border between Castasegna (CH) and Mese (IT). The planned Cable connection in 220 kV AC has a length of around 14 km, 13.5 of witch in Italy. In connection with the realisation of the project a Ra-tionalisation of the 380 and 132 kV Grid in the region Mese (Provincia di Sondrio) is planned. The expected NTC increase is around 200-250 MW. The Investement is composed by the purly Merchant line Project, around 45M€ and the TERNA Investment part for the rationalisation of the existing 380/132-kV Network and the Realisation of a new 380/132-kV Substation in Mese, other 45M€ Investment. | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | False | TYNDP 2016, 2018 and 2020 PDS Terna from 2011 till actual (2021) |  |  | Italy - Switzerland - 200 | Italy - Switzerland - 2200 - Italy - - 1000 - 5000 Switzerland - - <1000 | Switzerland - Italy | 200 | 200
252 | Internal Belgian Backbone Center-East: HTLS upgrade Massenhoven-VanEyck-Gramme-Courcelles-Bruegel-Mercator | This project structurally strenghtens the central & eastern part of the internal Belgian backbone. The current conductors on the 380kV ring Massenhoven-VanEyck-Gramme-Courcelles-Bruegel-Mercator-Massenhoven will be replaced by HTLS conductors. It follows a phased approach running up to 2038. Phasing is subject to optimalisation in function of outage constraints (operational security) and the evolution of the production park. This upgrade will be key to sustain price convergence whilst the power flows become increasingly more volatile and international. Where in the past the location of generation and load centers was quite stable over time, this will be much less the case with the future energy mix characterized by RES geographically spread out over Europe. Upgrading the existing internal corridors also ensures the potential to integrate new large power plants domestically. RES integration implies higher flows in the meshed AC-grid and thus increases the need for internal transmission capacity. This project contributes to adequacy, as both new grid hosting capacity is created & as it supports other projects intending to increase cross border transmission capacity. Uncertainty on sequence and timing due to potential nuclear prolongation. | Elia | BE | NDP1, Belgium, 2020-2030, §4.1.3 | 2038 | 2 | False | True | Upgrade | False |  | All investment items have been clustered together as they are seen collectively as a required grid reinforcement to avoid having internal bottlenecks on the Belgian transmission grid in the future. | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | False | More information about the projects can be found following these links: - HTLS-upgrade Massenhoven-Van Eyck: https://www.elia.be/en/infrastructure-and-projects/infrastructure-projects/massenhoven-van-eyck - National Development Plan: https://www.elia.be/-/media/project/elia/elia-site/infra-and-projects/investment-plans/federal-development-plan-2020-2030/nl/20190516_federaal-ontwikkelingsplan_nl.pdf?la=en | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | he upgrade of the backbone ring will unlock the full potential of future cross border capacity investments allowing higher market exchanges between bidding zones and leading to a higher price convergence in more hours of the year. This project contributes to adequacy, as both new grid hosting capacity is created and as it supports other projects intending to increase cross border transmission capacity, and in particular for Belgium considering the nuclear phase out. This project contributes to resolving internal congestions, considering expected increased market exchanges which induce higher flows. RES integration implies higher flows in the meshed AC-grid and thus increases the need for internal transmission capacity. This project satisfies this need in a cost-efficient manner. |  |  | Internal (Belgium) | 1500 | 1500
253 | Upstream reinforcement in France to increase FR-CH capacity | The project consists in attracting the flows to the interconnection south of Lake Geneva in order to alleviate the congestion on the link west to Lake Geneva. This project is coupled with Project 333 "PST Foretaille" and will be implemented right after the implementation of PST in Foretaille. | Rte | CH ;FR | SDDR (Schéma Décennal de Développement du Réseau -Ten Year Network Development Scheme), France, 2019, project n°446, page 442, https://www.rte-france.com/en/analyses-trends-and-perspectives/ten-year-network-development-plan#Documents | 2031 | 1 | True | False | MostlyNew | False |  | - | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | False |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | Figures 2.12 and 2.13 of IoSN 2020 Report: average marginal price difference higher than 10€/MWh between France and Switzerland in future scenarios. Project has positive impact on SoS indicator. Project upgrades the thermal capacity requested for meeting the French export increases that have an impact on French internal lines, such as Creys - St Vulbas. | France - Switzerland - 2500 | France - Switzerland - 3500 - France - - 1000 - 5000 Switzerland - - <1000 | Switzerland - France | 500 | 500
254 | HVDC Ultranet Osterath to Philippsburg | The Ultranet project consists of a 2 GW HVDC-connection from the Region of Osterath (Rhineland) to the Region of Philippsburg (Baden-Württemberg). It's a pilot project with DC circuits on the same py-lons as AC lines and will therefore deliver profund knowledge. The project forms the southern section of the so-called “Corridor A” concept (with project 132) fore-seeing connection of the northern and southern regions of Germany via HVDC power lines. As such, ULTRANET does reinforce the grid after nuclear phase-out. It also complies to the European North-South Interconnection idea aiming at connecting the significant offshore renewable generation capac-ities in the North Sea with the load centres in the southern parts of Europe. | Amprion, TransnetBW | DE | German NDP: Netzentwicklungsplan Strom 2035 Version 2021, Germany, Project No. DC2, p.391; https://www.netzentwicklungsplan.de/sites/default/files/paragraphs-files/NEP_2035_V2021_2_Entwurf_Teil2.pdf | 2026 | 3 | False | True | New | True | 2.9 |  | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | German Network Development Plan 2035 Version 2021: https://www.netzentwicklungsplan.de/sites/default/files/paragraphs-files/NEP_2035_V2021_2_Entwurf_Teil2.pdf 5th PCI-List: https://ec.europa.eu/energy/sites/default/files/fifth_pci_list_19_november_2021_annex.pdf 3rd PCI-list: https://ec.europa.eu/energy/sites/ener/files/documents/annex_to_pci_list_final_2017_en.pdf 4th PCI-List: https://ec.europa.eu/energy/sites/ener/files/c_2019_7772_1_annex.pdf Bundesbedarfsplan 2021 (BBPIG): https://www.netzausbau.de/Vorhaben/ansicht/de.html?cms_nummer=2&cms_gruppe=bbplg http://www.gesetze-im-internet.de/bbplg/BJNR254310013BJNE000605377.html Project specific websites: Amprion: https://www.amprion.net/Netzausbau/Aktuelle-Projekte/Ultranet/ TransnetBW: https://www.transnetbw.de/de/netzentwicklung/projekte/eichstetten-bundesgrenze-frankreich/projektueberblick | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Reduction of the loop flows occurrence in the borders between CZ-DE, DE-PL, DE-NL-BE-LU-FR-DE Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) | In connection with P132, the planned HVDC connection transports the energy of regenerative Energy sources in northern Germany directly to the demand regions of southern Germany. It strengthens the common German market area through targeted energy transport. The project reduces loop flows to Germany's neighboring countries by reducing bottlenecks in northern Germany and providing a transport task from western Germany to southern Germany. In combination with P132 the project enables the integration of offshore and onshore wind energy by preventing potential bottlenecks in northern and southern Germany. The project contributes significantly to security of supply and grid stability through the widespread integration of renewable energies in northern (wind offshore and onshore) and southern Germany (wind onshore). In particular, the system flexibility is increased by the use of HVDC converter. |  |  | Germany - France Internal (Germany) | 950 2000 | 650 2000
259 | HU-RO | 400 kV interconnection line between Hungary and Romania. In Romania, the following internal investments are necessary associated to this project: -new 400/220 kV transformer in substation Rosiori -reconductoring 220 kV OH line Urechesti-Tg. Jiu-Paroseni- Baru Mare-Hasdat | MAVIR, Transelectrica | HU ;RO | A Magyar Villamosenergia-rendszer Hálózatfejlesztési Terve 2017., Hungary, 2017, Page 6; The project is included in the Romanian NDP (Planul de Dezvoltare a RET 2022 - 2031) submitted in May 2022 for approval to the Romanian NRA , https://web.transelectrica.ro | 2030 | 2 | True | False | MostlyNew | False |  | The investments complement each other, the internal projects in Romania eliminating bottlenecks in the network and contributing to the increase of transfer capacity on the RO-HU border. Based on these information, it is essential to group all these investments together in order to utilize the possible benefits. | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | False | "The project was originally proposed by the ENTSO-E Common Planning Study performed during TYNDP 2016, which found potential when assessing against TYNDP 2014 Vision 4. The need was confirmed during the IoSN process of TYNDP 2018, in scenarios DG2040 and GCA2040 and during the IoSN process of TYNDP 2020" | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | According to ENTSO-E System Needs study for TYNDP 2022, the difference in the marginal cost of electricity between Romania and Hungary in 2040, in the No investment case is 10- 20 EUR/MW and with project case is 5-10 EUR/MW The ratio between nominal transmission capacity and installed RES capacity in 2030 in Romania increase from 25.5% in TYNDP 2022 DE2030 scenario without projects to 46% with projects and from 53.5% in TYNDP 2022 NT2030 scenario without projects to 96.4% with projects According to ENTSO-E System Needs study for TYNDP 2022, the increase of transfer capacity at the boundary between Romania and Hungary, will support the large scale integration of RES (the curtailed energy will decrease). | Hungary - Romania - 2027 | Hungary - Romania - 2027 - Hungary - - 1000 - 5000 Hungary - - 1659 | Romania - Hungary | 1117 | 685
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | This project considers a multi-purpose HVDC interconnection between Great Britain and The Netherlands, that combines the benefits of connecting electricity markets and offshore wind generation in Great Britain and The Netherlands. The base capacity of the cross border interconnection is around 2GW, but more can be considered. | National Grid, TenneT-NL | GB ;NL |  | 2030 | 1 | True | False | New | False |  |  | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | True |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between the Dutch and UK bidding zones. The possibility of higher market exchanges between these bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials. This leads to lower and more affordable prices for consumers. This project can improve system adequacy since it increases the interconnection capacity and also connects an offshore wind farm to the Dutch and UK systems. It contributes to connecting offshore wind in an efficient and faster way whilst reducing the number of landfalls and the subsequent disruption to local communities. By connecting offshore wind to the system, this project helps achieve future goals and scenarios for CO2 neutrality This multi-purpose interconnector will increase the interconnection capacity and also combine the connection of an offshore wind farm. This project will pave the way to connecting offshore wind farms in a different way, reduce connection costs and contribute to reaching the EU targets for offshore wind capacity expansion | The Netherlands - UK - 2000 | The Netherlands - UK - 2000 - The Netherlands - - 1000 - 5000 | United Kingdom - Netherlands | 2000 | 2000
263 | Lake Constance East | This project increases the capacity between CH and its neighbours DE and AT. This enables to connect large renewable generation in Northern Europe to consumers and pump storage devices in the Alps, thus noticeably increasing the mutual balancing between both regions. | Swissgrid, VUEN, Amprion, Transnet-BW | AT ;CH ;DE | Technischer Bericht zum Strategischen Netz 2025 (swissgrid.ch) , Switzerland, 2015 - NDP VUEN, Austria, NDP Nr. 4/2019, 16, http://www.vuen.at/ | 2035 | 1 | True | False | MostlyNew | False |  | The clustering of investments Rüthi - Bonaduz/Mettlen, Vorarlberg and Wullenstetten – Border Area (DE-AT) enables to show the full benefit of the project and to fulfil the transfer capacity increase (one investment cannot perform its intended function without the realization of the other investments). | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | False |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project contributes to lowering the price differentials between Switzerland, Germany and Austria. This project contributes to the adequacy in view of the nuclear phase-out and the development of renewables and pump hydro storage devices. This project is located in a highly meshed part of the transmission grid and therefore helps accommodate such flows. The project improves the accommodation of power flows by connecting high installed capacities of RES in Germany with pump storages in Austria and Switzerland. | Austria - Switzerland - 200 Germany - Switzerland - 1550 Austria - Germany - 3100 | Austria - Switzerland - 1200 - Germany - Switzerland - 1550 - Austria - Germany - 3100 - Austria - - <1000 Germany - - 5000 - 10000 Switzerland - - <1000 | Austria - Switzerland Switzerland - Germany Austria - Germany | 100 600 1000 | 200 250 1000
267 | Hansa PowerBridge II | Possible second HVDC cable interconnector between southern Sweden (Bidding area SE4) and Germany (50Hertz). This project candidate is driven by market based target capacities found in the Common Planning Studies by Regional Group Baltic Sea. | Svenska kraftnät, 50Hertz | DE ;SE | German NEP2035, version 2021, 2nd draft, Germany, 2021, project P221, p. 531-534, https://www.netzentwicklungsplan.de | 2035 | 1 | True | False | New | False |  |  | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | False | German NEP2035, version 2021, 2nd draft, Germany, 2021, project P221, p. 531-534, https://www.netzentwicklungsplan.de | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The main driver is market integration of the Nordic hydro/nuclear/RES dominated system with the German thermal/RES based system. The infrastructure will reduce price differentials between EU countries. The system adequacy is enhanced in Germany which will increase the import potential in period of low wind and solar generation. Also the system adequacy in southern Sweden is enhanced since it given more import capacity in a future with less available nuclear generation capacity. Increase of RES in both countries leads to higher need for trade with high surplus during high wind power production. Flows are to be balanced with southbound flow during peak hours and when hydro inflow in Sweden are high and northbound in periods of high German RES generation by night | Germany - Sweden - 1400 | Germany - Sweden - 2900 - Germany - - 5000 - 10000 | Germany - Sweden | 700 | 700
270 | FR-ES project -Aragón-Atlantic Pyrenees | This project consist of a new HVDC interconnection between France and Spain located in the Central part of the Pyrenees between Aragón region (Spain) and Marsillon (France). Internal AC reinforcements in Spain complement the cross border section, in order to connect the new converter station to the existing network. This project was included in the PCI list since 2015 (PCI 2.27.1) | Red Eléctrica, Rte | ES ;FR | French NDP, SDDR (Schéma Décennal de Développement du Réseau -Ten Year Network Development Scheme), France, 2019, project n°1039, page 442, https://www.rte-france.com/fr/article/evolution-du-reseau-electrique-francais-l-horizon-2035, Spanish NDP, "Plan de desarrollo de la red de transporte de energía eléctrica.Horizonte 2021-2026" Project Label INT_ESP-FRA_5: Interconexión España-Francia por los Pirineos (Aragón-Pirineos Atlánticos) pg439 | 2030 | 2 | True | False | New | True | 2.27.1 | Internal AC reinforcements in Spain complement the project, in order to connect the new converter station to the existing network. | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | False | - Spanish National Development Plan: https://www.planificacionelectrica.es/sites/webplani/files/2022-06/REE_Plan_Desarrollo.pdf and its project sheet platform: https://www.planificacionelectrica.es/proyectos - French National Development Plan http://www.rte-france.com/fr/article/schema-decennal-de-developpement-de-reseau - Inter-Governmental agreement (Madrid and Lisbon Declarations): https://ec.europa.eu/energy/sites/ener/files/documents/Madrid%20declaration.pdf https://ec.europa.eu/info/sites/info/files/lisbon_declaration_energyinterconnections_final.pdf - Constitution of the High Level Group on Interconnections for South West Europe: http://europa.eu/rapid/press-release_IP-15-5187_en.htm | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The IoSN report show high price differentials in FR-ES that would be reduced with a project in this border. IoSN report shows that for the 2040 time horizon there is need for developing projects in the French-Spanish border as the yearly average marginal price difference is higher than the 2€/MWh defined by Interconnection Target Expert Group as threshold for developing new interconnections. In addition, Spanish interconnectors nominal transmission capacity is below 30% of the national peak load and RES capacity. By increasing interconnection capacity on ES-FR border, the project contributes to enhance flow distribution and RES integration, and to increase exchanges between France and the Iberian Peninsula. TYNDP shows a reduction of RES spillage considering the increase of interconnection capacity in ES-FR boder. | France - Spain - 3000 | France - Spain - 4500 - France - - 1000 - 5000 Spain - - >10000 | Spain - France | 1500 | 1500
276 | FR-ES project -Navarra-Landes | This Project consist of a new HVDC interconnection between France and Spain in the Western part of the Pyrenees between Pamplona area (Spain) and Cantegrit (France). The project is considered as an HVDC project of 2x1000 MW. Internal reinforcements complement the cross border section. This project was included in the PCI list since 2015 (PCI 2.27.2) | Red Eléctrica, Rte | ES ;FR | French NDP, SDDR (Schéma Décennal de Développement du Réseau -Ten Year Network Development Scheme), France, 2019, project n°1039, page 442, https://www.rte-france.com/fr/article/evolution-du-reseau-electrique-francais-l-horizon-2035 Spanish NDP, "Plan de desarrollo de la red de transporte de energía eléctrica.Horizonte 2021-2026" Project Label INT_ESP-FRA_4: Interconexión España-Francia por los Pirineos (Navarra-Landes) pg436 | 2030 | 2 | True | False | New | True | 2.27.2 | The reinforcements of 400kV Cantegrit-Saucats and 225kV Cantegrit-Marsillon lines have a positive impact on the transfer capacity of the transpyrenean HVDC projects (P276 and P720) between Spain and France. Without these reinforcements, the capacity increase of each project would be less than the 1500 MW described below because of limitations on Cantegrit-Saucats and Cantegrit-Marsillon. Currently, they are associated with the project envisaged to date as arriving first, i.e. project p276. Nevertheless, the order of arrival of these two projects is still under study and has not been definitively decided. | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | True | - Spanish National Development Plan: https://www.planificacionelectrica.es/sites/webplani/files/2022-06/REE_Plan_Desarrollo.pdf and its project sheet platform: https://www.planificacionelectrica.es/proyectos - French National Development Plan: http://www.rte-france.com/fr/article/schema-decennal-de-developpement-de-reseau - Inter-Governmental agreement (Madrid and Lisbon Declarations): https://ec.europa.eu/energy/sites/ener/files/documents/Madrid%20declaration.pdf https://ec.europa.eu/info/sites/info/files/lisbon_declaration_energyinterconnections_final.pdf - Constitution of the High Level Group on Interconnections for South West Europe: http://europa.eu/rapid/press-release_IP-15-5187_en.htm | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The IoSN report show high price differentials in FR-ES that would be reduced with a project in this border. IoSN report shows that for the 2040 time horizon there is need for developing projects in the French-Spanish border as the yearly average marginal price difference is higher than the 2€/MWh defined by Interconnection Target Expert Group as threshold for developing new interconnections. In addition, Spanish interconnectors nominal transmission capacity is below 30% of the national peak load and RES capacity. By increasing interconnection capacity on ES-FR border, the project contributes to enhance flow distribution and RES integration, and to increase exchanges between France and the Iberian Peninsula. TYNDP shows a reduction of RES spillage considering the increase of interconnection capacity in ES-FR border. | France - Spain - 3000 | France - Spain - 4500 - France - - 1000 - 5000 Spain - - >10000 | Spain - France | 1500 | 1500
280 | FR-BE: study Lonny-Achene-Gramme | The project aims at sustaining further market integration within the long-term perspective of the energy transition and subsequent need to develop interconnection capacity on the French-Belgium border whilst alleviating Lonny-Achene-Gramme as bottleneck.The reinforcement strategy consists of maximizing the potential of the 400kV interconnector Lonny-Achene-Gramme through the use of cost-efficient technologies such as PSTs and HTLS as well as the possibility to rebuild Lonny-Achene-Gramme as a 2-circuit solution. The bilateral study will determine the appropriate implementation option and phasing of this implementation (for example: first install a PST, then upgrade the line capacity), taking into account 1) the optimization of flows between the 400kV interconnectors Avelin-Avelgem-Horta & Lonny-Achene-Gramme 2) that by 2025 Lonny-Achene-Gramme is a structural bottleneck due to the planned nuclear phase out in Belgium, and as such a first implementation step (for example PST) is needed 3) gain in efficiency in developing a structure with 2 circuits versus current structure with 1 circuit on Lonny-Achene-Gramme Project motivation: With this project RTE and Elia investigate the possibilities to further develop interconnection capacity on the FR-BE border, in line with the signals provided by the 2030 interconnection target criteria as well as the identification of needs upon 2040 scenario's, illustrating that higher power flows will emerge from future production mixes with more RES. This project fits within the strategy to develop cost efficient upgrades of the existing AC interconnectors in the CWE area. | Elia, Rte | BE ;FR | NDP1, Belgium, 2020-2030, §4.2.2.2 - NDP2, France, SDDR (Schéma Décennal de Développement du Réseau -Ten Year Network Development Scheme), 2019, project n°1050, page 442, https://www.rte-france.com/en/analyses-trends-and-perspectives/ten-year-network-development-plan#Documents | 2030 | 1 | True | False | MostlyUpgrade | True | 2.32 |  | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | True | More information about the project can be found following this link: - National Development Plan: https://www.elia.be/-/media/project/elia/elia-site/infra-and-projects/investment-plans/federal-development-plan-2020-2030/nl/20190516_federaal-ontwikkelingsplan_nl.pdf?la=en | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between Belgium and France. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours yearly and reduces therefore the price differentials. This is also included as key trigger of the 2030 interconnection criteria. Based on IOsN report, 15% IC-target requires higher cross border transmission capacity. This project contributes to satisfy this need, provided that the project benefits outweigh its costs. With the potential use of PSTs to better balance flows between the different crossborders lines, it will reduce bottlenecks and consequently increase the exchanges on the boundary itself and also in CWE area. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. | Belgium - France - 1000 | Belgium - France - 2000 - Belgium - - <1000 France - - 1000 - 5000 | Belgium - France | 1000 | 1000
283 | TuNur Italy | TuNur Italy is a 2,000MW HVDC transmission system that will enable the delivery of 13TWh/yr of low-cost controllable solar power to European consumers under long-term CPPAs. The transmission project will connect a dedicated hybrid solar facility in Southern Tunisia, where solar resources are extremely high enabling the most efficient integration of solar PV coupled with 15h of thermal storage, to the Montalto di Castro 400kV substation in Italy, the identified connection point on Terna's HV network. The HVDC transmission architecture is based on two independent bipolar +/-525kV systems of 1GW, with VSC HVDC Converter station technology ensuring high reliability and efficiency of the system. Each bipole will consist of a DC overhead line to the landfall point in Northern Tunisia; a submarine DC cable to the shoring point at Montalto di Castro; two HVDC converter stations; and a short 400kV AC cable from the converter station to Terna's 400kV substation. The project will enable the integration of massive amounts of RES; create significant carbon dioxide reductions; improve security of supply through diversification of supply; and support Europe's Green Deal and the REPowerEU objectives. | TuNur Ltd | IT ;TN | The project is mentioned in the Italian “Piano di Sviluppo”, Terna S.P.A. E Gruppo Terna of 2021 at page 262. There is no project number allocated to the project. The development plan can be found at: https://download.terna.it/terna/Piano_Sviluppo_2021_8d94126f94dc233.pdf | 2028 | 1 | True | False | New | False |  | To connect to Terna’s grid, the main investment (DC cable) requires a short AC cable. The AC cable has no standalone purpose without the main investment. | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | False | https://www.tunur.tn/project/tunur-italy-transmission-line/ | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) | TuNur will contribute to improving market integration and reducing price differentials between EU and non-EU countries by providing an additional 2000 MW of low cost and low carbon available capacity through a new connection between a non-EU (Tunisia) and EU (Italy) country. TuNur will provide dispatchable low-carbon power, thereby mitigating the risk of power failure, and will contribute to system adequacy deficiencies by increasing transmission capacity. This power source will improve security of supply by reducing Loss of Load durations across EU networks making a significant contribution to system stability The TuNur project will significantly contribute to system flexibility through direct access to a new source of renewable energy. TuNur will also contribute to system stability by improving transient stability and helping to meet RoCoF system needs. TuNur will provide flexible power with black-start capacity. TuNur consists in infrastructure that will contribute to balancing flexibility by providing the European network with a new source of low-carbon dispatchable power. Additionally, the TuNur project will deliver a 2000 MW power reserve through a new HVDC interconnection between Tunisia and Italy. |  |  | Italy - Tunisia | 2000 | 2000
285 | GridLink | 1.4 GW HVDC electricity interconnector between UK and France Voltage Source Converter (VSC) Grid connection point (substations name): Kingsnorth (UK) and Warande (France) Total cable length (substation to substation) 158km (110km in UK and 48km in France) Two cables (MI) laid in a single trench Nominal voltage: ±525 kV Thermal limit (Imax): 1330 A Mvar capability range at terminals: 460 MVAr Bus-bar to bus-bar losses profile over MW range: 2.3% (33 MW) full load; 0% (0 MW) at zero load Annual Availability: 98% availability, 2% planned outages, 0% forced outages. Maximum single failure according to the design: 1.4GW UK Transmission network reinforcement required: Uses spare bay with minimum works at Kingsnorth substation France transmission network reinforcement: New substation next to existing Warande substation Main environmental impact: reduction of CO2 emissions by substituting electricity from fossil fuels by generation from RES and nuclear power. No material environmental impacts during construction and operation. | iCON Infrastructure | FR ;GB | RTE Ten-Year Electricity Grid Development Plan 2020 (Schéma Décennal de Développement du Réseau (SDDR)), RTE Bilan prévisionnel 2021 and TYNDP 2020 | 2025 | 3 | True | False | New | False |  |  | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | False | Project web-site: www.gridlinkinterconnector.com/ Statement on unbundling pursuant to Appendix 6.1.1 of the Practical Implementation Guide dated 2 October 2017: "GridLink Interconnector will abide by the European rules governing unbundling pursuant to the 3rd Energy Package." | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment |  | France - UK - 4800 | France - UK - 4800 - France - - 1000 - 5000 | France - United Kingdom | 1400 | 1400
286 | Greenlink | An electricity interconnector between Ireland and Wales, Greenlink brings significant benefits on both sides of the Irish Sea for energy security and the integration of renewable low carbon energy sources. For Ireland, it provides a natural link to the EU and Nordic electricity markets via Wales, England and Scotland. Greenlink will employ proven HVDC technology and is similar to the successful East West Interconnector between North Wales and Ireland. The cable route will run from existing substations in Great Island, Co. Wexford and Pembrokeshire in Wales connecting EirGrid and National Grid power systems. It is unobtrusive, being underground subsea cables with a converter station located at each connection point. Both Ireland and the UK have stated their support for increased interconnection and its strategic benefits. | Greenlink Interconnector Limited | GB ;IE | Greenlink is included in EirGrid’s Draft Transmission Development Plan 2020-2029 (page 72-73 and Table A-2 and Table A3): https://www.cru.ie/wp-content/uploads/2021/04/CRU21048a-EirGrids-draft-Transmission-Development-Plan-TDP-2020-29.pdf Greenlink is included as a contracted interconnector in National Grid’s Interconnector Register dated 24 September 2021 (line item 16) (https://www.nationalgrideso.com/industry-information/connections/reports-and-registers), which is further referenced in the National Grid Electricity Ten Year Statement 2020 (Appendix H, page 4): https://www.nationalgrideso.com/document/181481/download | 2024 | 4 | True | False | New | False |  |  | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | For up to date project information see the web site: https://www.greenlink.ie/ Greenlink is included in the 4th list of PCI projects. Greenlink received funding support from Connecting Europe Facility as follows: o April 2015 – December 2016 for up to 50% of €1,619,090 for an Action to conduct a series of environmental studies & surveys and address the regulation, grid and financial aspects of Greenlink. o April 2018 – September 2019 for up to 50% of €9,525,914 for an Action to submit permitting documents, carry out onshore and offshore surveys and studies and to address regulatory, grid and financial aspects of Greenlink o October 2018 – December 2020 for up to 50% of €7,200,646 for an Action to complete the remaining major development activities to reach financial close Greenlink is included as a contracted interconnector in National Grid’s Interconnector Register dated 24 September 2021 (line item 16), which is further referenced in the National Grid Electricity Ten Year Statement 2020 (Appendix H, page 4). In March 2021, Ofgem issued a letter confirming the socio economic benefits of Greenlink are still in the interests of the GB consumer. Greenlink is included in EirGrid's Draft Transmission Development Plan 2020-2029 (page 72-73 and Table A-2 and Table A3). In July 2019, the Irish Department of Communications, Climate Action and Environment (DCCAE) published a Climate Action Plan setting out the Irish government’s ambitious renewable energy target of 70% electricity from offshore wind, onshore wind, solar and other renewable technologies by 2030. The plan includes indicative targets of at least 3.5GW of offshore renewable energy, up to 1.5GW of grid-scale solar energy and up to 8.2GW total of increased onshore wind capacity. The plan recognised the importance of increased interconnection in achieving those goals. Greenlink entered into a connection agreement with EirGrid in November 2019. This is one of the critical pieces in the jigsaw of a project with wide-ranging political support, technical feasibility and excellent value-for-money for consumers. In October 2018 the CRU determined that Greenlink has the potential to provide net benefits to the consumer and Ireland as a whole and as such Greenlink passes the public interest test. The CRU granted Greenlink an Irish electricity interconnector operating licence in February 2022. | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) | Greenlink connects Ireland with GB enabling significant additional flows of 500MW (vs 1000MW existing capacity EWIC and Moyle) to reduce price differentials, especially those resulting from medium to high wind and low demand in the Irish single electricity market (i-SEM) which occurs frequently overnight The addition of 500MW import capacity into Ireland greatly improves the security of supply situation in times of reduced generation availability when the ability to meet the system demand is at risk. 500MW of increased interconnection potentially creates additional system demand which will reduce RES curtailment at times of high RES volumes. The TSO's in both IE and GB will have the ability to dispatch the reactive power capability of the Greenlink interconnector. | Island of Ireland - UK - 1450 | Island of Ireland - 1954 - Ireland - - 1000 - 5000 | United Kingdom - Ireland | 500 | 500
293 | Southern Aegean Interconnector | The project refers to the construction of a submarine DC transmission link to connect the licensed RES plants, located on 23 small uninhabited islands at the South Aegean sea, with mainland Greece and the islands of Crete and Kos (Dodecanese). The main link will be an HVDC link connecting the island of Levitha to both the metropolitan area of Athens and the island of Crete; the 400kV substation at Lavrion area will be the connection point in the Athens area and the substation of Atherinolakkos will be the connection point in Crete (located in the South-East coast). The capacity of each link will be 600 to 800MW both directions using HVDC (High Voltage Direct Current) XLPE insulated technology and both links will consist of two parallel cables in order to increase the reliability of each link. Three conversion stations using HVDC VSC technology are foreseen in Lavrio, Levitha & Crete (Atherinolakkos). All the installations on the islands (converter stations, substations etc) will be of closed type using GIS technology. The project will provide 19TWh/year of wind energy, increasing the transfer capacity between mainland Greece, Crete and Dodecanese islands. | Southern Aegean Interconnector SMSA (Member of Eunice Energy Group) | GR |  | 2025 | 1 | False | True | New | False |  | The clustering explanation is that the whole project refers to the construction of one common submarine DC transmission link to connect the licensed RES plants at the South Aegean Sea to mainland Greece and the islands of Crete, Kos and the Dodecanese. The main link will be an HVDC link connecting the island of Levitha to both the metropolitan area of Athens and the island of Crete. | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | False | http://eunice-group.com/projects/aegean-project/ | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure designed to offer more supply options to isolated areas Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. | Τhrough synergies with other PCI candidate projects and the ongoing promotion of Crete to an energy hub of the region capacity increase will be achieved with EU Member State of Cyprus (EuroAsia Interconnector - project 219), Egypt and North Africa (GAP Interconnector – project 1048). Significant RES increase expected by 2030 in Greece (intermittent RES installed capacity reaching 25,000MW according to the revised NECP) exceeding the relevant 50% system needs threshold. Ending energy isolation – Connecting isolated island systems of the Aegean Sea with mainland Greece plus fuel diversification. SAI formulates an extra transmission corridor that can benefit the generation adequacy and security of non interconnected island regions and Crete. |  |  | Greece - Bulgaria Greece - Italy Internal (Greece) | 0 0 582 | 0 0 582
297 | BRABO II + III | Realization of a new 380 kV corridor between Zandvliet and Mercator consisting of a double-circuit AC overhead line, including a new substation 380kV in Lillo. Project motivation: BRABO II and III sustain the development of interconnection capacity on the Belgian North Border towards a broader scenario framework, hereby securing the supply of electricity around the Antwerp harbour area in light of the increasing industrial demand (mainly applicable to BRABO II), as well as developing capacity for the potential integration of new production in the Antwerp area (mainly aplicable to BRABO III). This project contributes to resolving internal congestions, considering expected high international transit & loop flows. This project increases the degree of interconnectivity between the Belgian and Dutch bidding zone. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials.This project allows to deal with the growth in industrial consumption from the Antwerp harbour and to increase the grid hosting capacity for connection of new production capacity, thereby contributing to the overall adequacy of the system, especially relevant considering the nuclear phase out in Belgium.RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. | Elia | BE | NDP1, Belgium, 2020-2030, p.193, ID 29-and 32 | 2025 | 4 | False | True | New | True | 2.23 | The projects have been clustered because all together they create a NTC increase on the border between the Belgian and Dutch bidding zone. | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | More information about the project can be found following these links: - https://www.elia.be/en/infrastructure-and-projects/infrastructure-projects/brabo - https://www.elia.be/en/infrastructure-and-projects/infrastructure-projects/brabo-lll - National Development Plan: https://www.elia.be/-/media/project/elia/elia-site/infra-and-projects/investment-plans/federal-development-plan-2020-2030/nl/20190516_federaal-ontwikkelingsplan_nl.pdf?la=en | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between the Belgian and Dutch bidding zone. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials This project allows to deal with the growth in industrial consumption from the Antwerp harbour and to increase the grid hosting capacity for connection of new production capacity, thereby contributing to the overall adequacy of the system, especially relevant considering the nuclear phase out in Belgium. This project contributes to resolving internal congestions, considering expected increased market exchanges inducing higher flows. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. |  |  | Belgium - Netherlands | 1000 | 1000
299 | SACOI3 | New HVDC line between Italy mainland, Corsica and Sardinia replacing existing link SACOI2. Due to an update of the list of cross-border projects interconnecting Italy with other Member States within 2020, the 2020 interconnection ratio of Italy has been updated accordingly (from previous value of 9% computed by ENTSO-E in TYNDP 2018 to roughly 8%). As the Interconnection level of 10% will not be reached by 2020, Italy is requested to investigate options of further interconnections. | Terna, EDF | FR ;IT | Piano di Sviluppo 2021 – Avanzamento Piani di Sviluppo Precedenti – Avanzamento Nord Ovest, Italy, 2021, ID: 301-P, pag. 26, https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete | 2027 | 3 | True | False | Upgrade | True | 2.4 |  | TYNDP 2016 ;TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project contributes to lowering the price differentials between Italian and Corsica market zones This project helps Italy to reach the 15% interconnection target by 2030 This project will contribute to overcome flexibility/stability problems due to scarsely meshed grid This project will improve the integration of italian RES generation | Italy - Corsica - 100 | Italy - Corsica - 100 - Corsica - - 123 Corsica - - <1000 Italy - - 1000 - 5000 | Internal (Italy) | 400 | 400
309 | NeuConnect | NeuConnect will be the first subsea HVDC electricity Interconnector to connect the UK and German electricity markets. It will be approximately 700km long with a capacity of 1.4GW. NeuConnect is a new interconnector under development that will create the first direct link between the countries by connecting the markets for the first time and is forecasted to deliver significant consumer benefits and will deliver a 16 million tonne reduction in CO2 emissions over 25 years. This approach offers clear benefits on both sides by reducing costs for consumers whilst increasing consumer choice and offering the best choice for fighting climate change. | NeuConnect Britain Limited, NeuConnect Deutschland GmbH | DE ;GB | Germany - Bedarrfsermittlung 2019-30 Measure M534 Fedderwarden – Großbritannien (NeuConnect) Leitung United Kingdom - National Grid - NeuConnect appears in the Interconnectors Connection Register www.nationalgrideso.com/connections/registers-reports-and-guidance | 2027 | 3 | True | False | New | False |  | NeuConnect is an Independent Interconnector and not connected to any other transmission project. | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | https://neuconnect-interconnector.com | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) | Neuconnect helps reduce price differentials as it adds significant cross border transmission capacity being the first Interconnector between the United Kingdom and Germany. NeuConnect will contribute 1400MW of interconnection capacity to the 15% interconnection targets of the UK and Germany whilst simultaneously facilitating the higher levels of RES integration into the respective transmission networks and reducing internal transmission constraints. The UK and Germany generate significant RES in the form of solar and wind. This high capacity, flexible HVDC interconnector will facilitate greater integration and distribution of energy from these sources. This high capacity HVDC connection between the UK and Germany utilises sophisticated Voltage Source Control(VSC) power converter technology enabling flexible grid services including reactive power and will provide both additional voltage stability and security of supply benefits and support market integration. | Germany - UK - 1400 | Germany - UK - 2800 - Germany - - 5000 - 10000 | Germany - Untied Kingdom | 1400 | 1400
312 | St. Peter (AT) - Tauern (AT) | This project is part of the Austrian 380-kV security ring. It therefore provides based on the concept a redundant and robust connection and increases security of supply significantly. In addition higher transport capacities are able to connect RES production in the corners of the region with the Alpine storages and therefore integrate both efficiently and properly. | Austrian Power Grid | AT | APG Netzentwicklungsplan 2021, AT, 2021, 11-10, 48, https://www.apg.at/de/Stromnetz/Netzentwicklung | 2025 | 4 | False | True | New | True | 3.1.2 |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | PCI 3.1.2: 3rd List: https://ec.europa.eu/energy/sites/ener/files/documents/annex_to_pci_list_final_2017_en.pdf 4th List: https://ec.europa.eu/energy/sites/ener/files/c_2019_7772_1_annex.pdf National development plan: https://www.apg.at/en/Stromnetz/Netzentwicklung Project Homenpage: https://www.apg.at/en/Projekte/380-kV-Salzburgleitungg | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | facilitates interconnection capacity Interconnection between huge amounts of RES and storage capacity in the Alps provides flexibility and stability. Interconnection between huge amounts of RES and storage capacity in the Alps helps to reduce the amount of RES curtailment significantly |  |  | Austria - Germany Internal (Austria) | 1359 2000 | 1422 2000
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | New 380kV Line between TenneT-DE and APG (Isar/Altheim/Ottenhofen - St. Peter). This project reinforces the interconnection capacity between Austria and Germany. It supports the interaction of RES in Northern Europe (mainly in Germany) and in the eastern part of Austria with the pump storages in the Austrian Alps and therewith facilitates their utilisation. | Austrian Power Grid, TenneT DE | AT ;DE | DE: NEP2035 v2021 p. 357 ff; APG Netzentwicklungsplan 2021, AT, 2021, 11-7, 58, https://www.apg.at/en/Stromnetz/Netzentwicklung | 2026 | 3 | True | False | New | True | 3.1.1 |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | Third PCI List: https://ec.europa.eu/energy/sites/ener/files/documents/annex_to_pci_list_final_2017_en.pdf https://ec.europa.eu/energy/sites/ener/files/c_2019_7772_1_annex.pdf NDP Austria: http://www.apg.at/de/netz/netzausbau/Netzentwicklungsplan NDP Germany: www.netzentwicklungsplan.de Project homepage Austria: https://www.apg.at/en/projekte/380-kv-deutschland-leitung | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | helps to reach 15% target in Germany high RES generation connected to pump storage high RES generation connected to pump storage |  |  | Austria - Germany | 2000 | 2000
323 | Dekani (SI) - Zaule (IT) interconnection | The Zaule (IT) - Dekani (SI) interconnection is a third party cross-border electrical line promoted by Adria Link Srl, E3, ENERGETIKA, EKOLOGIJA, EKONOMIJA, d.o.o.. and Holding Slovenske Elektrarne d.o.o.. The project concerns an underground cable 110kV a.c. merchant line, 150 MW from Zaule (IT) substation to Dekani (SI) substation, including a 110/135 kV Phase Shifter Transformer. | HSE d.o.o. (Holding Slovenske Elektrarne, d.o.o.) - E3 d.o.o. (ENERGETIKA, EKOLOGIJA, EKONOMIJA, d.o.o) - Adria Link Srl | IT ;SI |  | 2025 | 3 | True | False | New | False |  |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The Project will increase the cross-border capacity between the interconnected Countries and will allow market exchanges which lead to a minimising price differentials of the Italian border also in line with the interconnection target recommendations (Nov 2017) by EC Expert Group. The project will enhance the adequacy of the interconnected systems in the mid/long-term scenarios with a different generation mix . In particular, it improves the share of the renewable energy sources and new flexible thermal generation in the electricity systems involved by the line. The Project contributes to increase the Italian cross-border capacity in the medium-long term objectives (2030) as also reported in the Italian Implementation Plan for the requirements set in article 20 of Regulation 2019/943 of 5th June 2019 on the Internal Electricity Market (IEM). This cross border project allows higher flows in the meshed AC-grid and consequentially it allows better integration of RES in the interconnected Countries. | Italy - Slovenia - 125 | Italy - Slovenia - 125 - Italy - - 1000 - 5000 | Italy - Slovenia | 0 | 40 | Regarding the “Transfer capacity increase (in MW)” in the "Project Description & Context" tab, Promoter wishes to point out that the values indicated by the TSOs (Terna and Eles) were calculated in 2019 by taking into account the lower NTC values defined by each TSO on the basis of the grid configuration as of 2019. Please note that, on the Italian side, the calculation was performed according to Art. 9 of Italy’s “Legislative Decree of 21 October 2005” that for the NTC calculation considers the structure of the national transmission grid, the interconnected foreign grid, as well as the projects under construction at the date. In other terms, it is not a projection at one point in time in the future, i.e. it does not take into account the development programs of the countries involved. Regarding the “Transfer capacity increase (in MW)” in the "Project Description & Context" tab, Promoter wishes to point out that the values indicated by the TSOs (Terna and Eles) do not refer to any formal act by NRAs and/or the European Commission.
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | "The Redipuglia (IT) - Vrtojba (SI) interconnection is a third party cross-border electrical line promoted by Adria Link Srl, E 3, ENERGETIKA, EKOLOGIJA, EKONOMIJA, d.o.o. and Holding Slovenske Elektrarne d.o.o.. The project concerns an underground cable 110kV a.c. merchant line, 150 MW from Redipuglia (IT) substation to Vrtojba (SI) substation, including a 110/135 kV Phase Shifter Transformer." | HSE d.o.o. (Holding Slovenske Elektrarne, d.o.o.) E3 d.o.o. (ENERGETIKA, EKOLOGIJA, EKONOMIJA, d.o.o) Adria Link Srl | IT ;SI |  | 2024 | 3 | True | False | New | False |  |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The Project will increase the cross-border capacity between the interconnected Countries and will allow market exchanges which lead to a minimising price differentials of the Italian border also in line with the interconnection target recommendations (Nov 2017) by EC Expert Group. The project will enhance the adequacy of the interconnected systems in the mid/long-term scenarios with a different generation mix . In particular, it improves the share of the renewable energy sources and new flexible thermal generation in the electricity systems involved by the line. The Project contributes to increase the Italian cross-border capacity in the medium-long term objectives (2030) as also reported in the Italian Implementation Plan for the requirements set in article 20 of Regulation 2019/943 of 5th June 2019 on the Internal Electricity Market (IEM). This cross border project allows higher flows in the meshed AC-grid and consequentially it allows better integration of RES in the interconnected Countries. | Italy - Slovenia - 125 | Italy - Slovenia - 125 - Italy - - 1000 - 5000 | Italy - Slovenia | 10 | 10 | Regarding the “Transfer capacity increase (in MW)” in the "Project Description & Context" tab, Promoter wishes to point out that the values indicated by the TSOs (Terna and Eles) were calculated in 2019 by taking into account the lower NTC values defined by each TSO on the basis of the grid configuration as of 2019. Please note that, on the Italian side, the calculation was performed according to Art. 9 of Italy’s “Legislative Decree of 21 October 2005” that for the NTC calculation considers the structure of the national transmission grid, the interconnected foreign grid, as well as the projects under construction at the date. In other terms, it is not a projection at one point in time in the future, i.e. it does not take into account the development programs of the countries involved. Regarding the “Transfer capacity increase (in MW)” in the "Project Description & Context" tab, Promoter wishes to point out that the values indicated by the TSOs (Terna and Eles) do not refer to any formal act by NRAs and/or the European Commission.
325 | Obersielach (AT) - Podlog (SI) | Obersielach (AT) - Podlog (SI); 380-kV Upgrade; +500 MW NTC in both directions | Austrian Power Grid, Eles | AT ;SI | CD not in the NDP 10 year time frame. | 2034 | 1 | True | False | Upgrade | False |  |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | False | ENTSO-E TYNDP 2020: https://tyndp2020-project-platform.azurewebsites.net/projectsheets/transmission/325 | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Project increases capacity of SI-AT border and decreases price difference between both markets in all future scenarios. This project will contribute to redution of system adequacy deficiencies by increasing transmission capacity on SI-AT border. This project improves the integration of RES generation into the Continental European transmission grid. | Austria - Slovenia - 1000 | Austria - Slovenia - 1500 - Austria - - <1000 | Austria - Slovenia | 500 | 500
328 | Interconnector DE-LUX | The project comprises the construction of two new 380/220-kV-substations in Germany (Aach) and Luxemburg (Bofferdange). The new substations will be connected via a new AC-link to allow a higher cross border capacity between Germany and Luxembourg. | Amprion, Creos | DE ;LU | NDP1; Germany, Netzentwicklungsplan 2035 Version 2021, Project 406, p. 623; NDP Luxembourg 2040 Version 2021 p.28 & 29 | 2026 | 2 | True | False | New | False |  | The new AC double circuit overhead 400 kV line between Germany and Luxembourg is clustered with substation Aach (DE) and Bofferdange (LU) to secure the needed capacity and distribute the energy into lower voltage levels. The existing 220 kV OH-lines Trier-Blooren and Quint-Heisdorf will be decommissioned after the 400 kV OH lines and substations will be put in operation. | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | The project was part of the previous TYNDP 2020, Link to the Website: https://tyndp2020-project-platform.azurewebsites.net/projectsheets/transmission/328 A dedicated Website describing the 380 kV reinforcements are available under following link: www.creos.net/380 In line with Scenario report 2040 http://www.creos-net.lu/actualites/actualites/article/scenario-report-2040-public-consultation.html The existing 220-kV-line between Heisdorf/Blooren - Niederstedem/Quint will be partially dismantled after commissioning of this project. https://www.netzentwicklungsplan.de/de/projekte/projekte-nep-2035-2021 https://www.creos-net.lu/fileadmin/dokumente/NEWS/pdf/2020-2022/20210820_Network_Development_Plan_2040_-_HV_Transport_Grid__final_.pdf | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. |  | Germany - Luxemburg - 400 | Germany - Luxemburg - 400 - Germany - - 5000 - 10000 Luxemburg - - <1000 | Germany - Luxembourg | 1000 | 1000
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | The development of ~6 GW transport capacity through the elaboration of a new corridor in the western part of Belgium, between the Stevin axis and the Izegem substation. It is to be complemented with an HTLS upgrade of the existing Izegem/Avelgem connection. Along this corridor a substation functioning as 'gateway' for the evacuation of offshore potential is envisioned. This corridor is envisioned to be implemented in AC technology following the example of the Stevin project. Timing, routing, scope, etc. subject to feasibility studies and subsequent spatial planning procedures. The capacity of the Stevin axis will be fully used by 2020 for the integration of the first wave of 2.3 GW offshore wind in the Belgian North Sea and Nemo Link. A further development of the 380 kV grid via a new corridor towards the coast creates the necessary perspective to unlock the energetic potential of the North Sea beyond 2020, including but not limited to the development of additional offshore wind in the Belgian part of the North sea. This new corridor will be linked to the Stevin corridor, creating a meshed 380 kV grid structure and considerably increasing the reliability. | Elia | BE | NDP1, Belgium, 2020-2030, §4.1.5 page 10 | 2028 | 3 | False | True | New | False |  |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | More information about the project can be found following these links: - Project site: https://www.elia.be/en/infrastructure-and-projects/infrastructure-projects/ventilus - National Development Plan: https://www.elia.be/-/media/project/elia/elia-site/infra-and-projects/investment-plans/federal-development-plan-2020-2030/nl/20190516_federaal-ontwikkelingsplan_nl.pdf?la=en | Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This projects foresees the installation of phase shifting transformers enabling power flow control and optimizing the use of existing infrastructure. This project contributes to resolving internal congestions, considering expected high international flows as well as internal grid flows due to increased market exchanges. This project creates the necessary onshore grid capacity to facilitate offshore wind development. This project will facilitate further offshore development and create grid hosting capacity for onshore and offshore RES development. |  |  | Internal (Belgium) | 6000 | 6000
330 | 4th 400kV CZ-SK interconnector | This new 400 kV cross-border overhead line between the substations Otrokovice (CZ) - Ladce (SK) will strenghten the transmission capacity between Slovak and Czech transmission systems, aiming to maintain secure operation of both transmission systems. | CEPS, SEPS | CZ ;SK | This project is included in the last approved Slovakian NDP (SEPS). This project is not included in the last approved Czech NDP (CEPS) as the Czech Energy Act requires to have in NDP only projects which are commissioned in the ten-year time frame of the NDP. | 2035 | 1 | True | False | New | False |  | The new 400kV CZ-SK cross-border single OHL Otrokovice (CZ) - Ladce (SK) aims to increase NTC at the CZ-SK cross-border profile. The new 400kV substation Ladce (SK) is clustered with the CZ-SK cross-border line into one projects as it is directly connected into the new 400kV substation Ladce (SK). | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | False | Environmental Impact The over-headline project Otrokovice - Ladce is included in the Czech Land Use Development Policy which is the land use plan for the entire country adopted on 15th April 2015 by the Czech government under the governmental resolution. The proposed route (corridor) of the over-headline on the Czech territory was chosen with respect to the municipalities' land plans, transport and technical infrastructures and other development plans of regional importance (local roads, highways, railways, other transport and technical infrastructures). For the purpose of finding a suitable route, a spatial – land oriented technical study was carried out that evaluated several route variants with consideration of several aspects including environmental ones. The proposed route was then communicated with relevant and respective local and regional authorities, municipalities and other technical infrastructure owners. The outputs from the above study will be taken as an important input into the environment impact assessment which is scheduled to be conducted between 2022 and 2023 in accordance with EIA legislation. The main proposed route of the over-headline including its local variants on the Czech side does not pass through any NATURA 2000 sites. No bird areas and no European sites of interest are affected (EVL). The nearest locality EVL is EVL CHKO Beskydy (CZ 0724089) in the neighbourhood of Střelná village, to which one section of the route is approaching at the distance of about 93 m at the crossing point on the Czech-Slovakian border. According to the opinion of the Department of Environment and Agriculture of the Regional Authority of the Zlín Region granted on 22nd May 2017, the route of the new over-headline on the Czech side does not pass through the territories of European significant sites and bird areas (NATURA 2000). On the Slovak side this projects aims to replace the existing out-of-date 220kV interconnections between SK and CZ which are planned to be decommissioned in next ten years. For the purpose of its erection (not only) SEPS and CEPS have signed the Memorandum of understanding in order to efficiently coordinate the development activities on the common SK – CZ cross border profile. On the Slovak side the route for the purpose of the OHL erection is reserved in the spatial planning documents of the respective communities (villages, towns, county, etc.). The environmental impact assessment study will be carried out according to the particular Slovak legislation. SEPS does not expect any objection to get an approval from the environmental point of view, as the planned route of the line is the same as the existing 220 kV SK-CZ cross-border line corridor. Currently expected date of commissioning is in year 2035 which is also written in the above mentioned MoU. The new substation 400 kV Ladce (SK) needs to connect this OHL into the Slovak transmission system. Social impact: From the point of view of reliability of power supply in the Zlín region on the Czech side the construction of the over-headline Otrokovice – Ladce is very important because it will strengthen the connection of the Otrokovice substation to the transmission system. Otrokovice substation with three transformers 400/110 kV each with 350 MVA is currently connected to the transmission system with only two over-head lines. The energy transferred between the transmission and distribution system by this substation represents approximately about 7% of the total energy transferred between the transmission system and all distribution companies in the Czech Republic. From the above, it is obvious that strengthening the connection of substation Otrokovice with the transmission system is vital because it will ensure energy supplies to industry and a considerable number of households in the Zlín Region, which is one of the most exposed area in the Czech Republic. Considering the long-term aspect of increasing the consumption and reducing the share of electricity production by traditional generation connected into the 110 kV distribution system, the demand on the power transmitted by the transmission system is further increased, and therefore its strengthening is crucial for the society. The project is aiming to replace the 220 kV system in the west-north Slovakia by the new 400 kV substation with the new 400/110 kV transformation. The connection of the third 400 kV line (cross-border line Otrokovice - Ladce) to the Ladce substation will significantly improve security and reliability of the Slovak power system operation in that region, as well as during maintenance of the transmission system equipment. In the connected 110 kV distribution grid a lot of households and important consumers are connected as well as important power plants providing heat to the households in the cold months and the hydro power plants on the Váh river. This will have a substantial benefit for the society living in the Žilina and Považská Bystrica agglomeration. | Infrastructure to reduce price differentials between EU and/or non-EU countries Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project provides possibility to utilize energy resources in one system when the other has energy scarcity due to extra market transfers (increase of NTC) on the profile SK - CZ which could lead to reduction of marginal price. The project replaces two decommissioned 220 kV interconnectors on the CZ - SK profile by new 400 kV line. In this way the secure operation of both transmission systems and the power exchange will be ensured. This project increases the NTC on CZ - SK profile and therefore facilitates the future need for cross-border flows and improves operational security. The project is aiming at facilitation of the power flows from the RES generation in the northern part of Europe and eastern part of CZ therefore promotes RES integration. | Czech Republic - Slovakia - 500 | Czech Republic - Slovakia - 500 - | Czechia - Slovakia | 500 | 500
333 | PST Foretaille | Installation of two PSTs in Foretaille that control the flow on the Foretaille - Verbois 220 kV double line. | Swissgrid | CH | Schéma décennal de développement du réseau, France, 2019, projet n° 446, page 442 https://www.rte-france.com/en/analyses-trends-and-perspectives/ten-year-network-development-plan#Documents | 2031 | 1 | False | True | New | False |  | no clustering | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | False |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | IoSN report: average marginal price difference higher than 10€/MWh between France and Switzerland in future scenarios. Project has positive impact on SoS indicator. Project upgrades the thermal capacity requested for meeting the French export increases that have an impact on French internal lines, such as Creys - St. Vulbas. | France - Switzerland - 2500 | France - Switzerland - 3500 - France - - 1000 - 5000 Switzerland - - <1000 | Switzerland - France | 100 | 1000
335 | North Sea Wind Power Hub | TenneT Netherlands, TenneT Germany, Energinet and Gasunie joined forces to develop a large scale European electricity system for offshore wind in the North Sea. The North Sea Wind Power Hub (NSWPH) consortium partners consider the project to be an important possible alternative path of an internationally coordinated roll-out towards accomplishing the green energy transition and achieving the Paris Agreement. Central to the vision is the construction of one or more hubs at a suitable location in the North Sea with interconnectors to bordering North Sea countries and between the hubs. The whole system may function as a hub for transport of wind energy, an interconnection hub to the connected countries, a working hub for offshore wind developers and a location for possible power-to-gas solutions. This project is a first building block in the hub-and-spoke concept (NSWPH) connecting up to 14 GW future offshore wind parks to the systems of Denmark, the Netherlands and Germany around 2035. | Energinet.dk, TenneT-NL, TenneT-DE | DE ;DK ;NL | The NSWPH was analysed in the last National Development Plan of Germany. In the Danish case, a future 'Strategic Investment Plan' will be developed and cover a 20-year period in which the NSWPH will be included. The NSWPH is presently analyzed in various feasibility studies at wider regional level. It builds on long-term system needs also identified in ENTSO-E’s Regional Investment Plan North Sea. Due to the strong internationally coordinated drive of this project, the concept has been first addressed in ENTSO-E’s TYNDP process. | 2035 | 1 | True | False | New | True | 1.19 | The North Sea Wind Power Hub investment items need to be clustered and thereby realized together to meet its full benefit. The investment items are mutually dependent on each other. Realizing one investment contributes to the realization of the full potential of another investment item. The intended system includes a distributed hub situation to enable different realization time lines in the different participating countries. Without the wind farm connections, the configuration would merely provide interconnection while the RES integration would still require additional (radial) connections to shore. And without the interconnection links, the concept would be a single hub to shore, while missing the opportunities of market integration and sharing of reserves. Presently all investments in the NSWPH project are ‘under consideration’, with a provisional commissioning for 2035. | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | False | https://northseawindpowerhub.eu/ https://www.youtube.com/watch?v=lBnWEK9IUn4 Roland Berger for the European Commission, DG-ENER; "North Seas Offshore Energy Clusters - North Sea Wind Power Hub"; 2018. Cost-effective transition of energy through sector coupling: • THE IMPORTANCE OF THE GAS INFRASTRUCTURE FOR GERMANY’S ENERGY TRANSITION – A model-based analysis, Frontier economics et al. 2018 http://frontier-economics.com/publication/der-wert-der-gasinfrastruktur-fuer-die-energiewende-deutschland/ • The Potential role of Power-to-Gas in the e-Highway2050, European Power to Gas Platform/DNV-GL 2017 http://europeanpowertogas.com/new-study-released-on-potential-role-of-power-to-gas-in-the-e-highway2050-study/ • VAWOZ 2040 study “Studie systeemintegratie wind op zee 2030-2040” by the Dutch Government : https://offshorewind.rvo.nl/blog/view/9d736052-eb25-4775-8c4d-062979d6efae/rapport-systeemintegratie-wind-op-zee-2030-2040-in-dutch Increasing the value of wind through the reduction of low electricity prices and curtailment: • System Perpective 2035 – Long-term perspectives for efficient use of renewable energy in the Danish energy system, Energinet 2018 https://en.energinet.dk/-/media/Energinet/Analyser-og-Forskning-RMS/Dokumenter/Analyser/_Analyser-Engelsk/System-Perspective-2035---Main-Report_English.pdf Demand for renewable H2 in countries of the Project Promotors • DE: Role of gaseous energy carriers in decarbonising Germany - Results of a brief meta-study of independent third party studies, Wagner, Elbling & Company 2018 • DK: System Perspective 2035 – Long-term perspectives for efficient use of renewable energy in the Danish energy system, Energinet 2018 (Danish Version) https://energinet.dk/-/media/4DDC27A7159245E985CEC07A92FB70AF.pdf • NL: Chemistry for Climate – Roadmap for the Dutch Chemical Industry towards 2050, Ecofys 2018 https://www.ecofys.com/files/files/vnci_routekaart-2050.pdf | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Connecting three countries (DE, DK and NL) in one project together with huge amounts of RES installation will help reducing the price differentials between the directly impacted countries but will also have an effect on the EU-wide energy system. o The project enables the direct installation and integration of vast amounts of offshore wind energy. Together with interconnecting three countries (DE, DK and NL) the project will both enable RES integrating and reducing RES curtailment. |  |  | Germany - Denmark/Netherlands | - | -
338 | Adriatic HVDC link | New HVDC line between Villanova (or Villavalle) and Fano (or Portotolle) existing 400 kV substations (the nominal power of the link will be at least 1000 MW) | Terna | IT | Piano di Sviluppo 2021 – Avanzamento Piani di Sviluppo Precedenti – Avanzamento Nord Est https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete/pag.29 | 2028 | 2 | False | True | New | False |  |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | True | Italian Development Plan: http://www.terna.it/it-it/sistemaelettrico/pianodisviluppodellarete/pianidisviluppo.aspx | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | The new line will allow congestion reduction on the Southern-Northern border, and the integration of the local renewable production. |  |  | Italian Northern border or Italy-Greece Internal (Italy) Internal (Italy) | 500-1000 600 1000 | 500-1000 1000 1000
339 | Tyrrhenian link | Italian HVDC link between Campania, Sicily and Sardinia | Terna | IT | Piano di Sviluppo 2021 – Avanzamento Piani di Sviluppo Precedenti – Avanzamento Nord Est https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete/page 32 | 2028 | 3 | False | True | New | False |  | the two investments will allow to increase the transmission transport capacity between Italian main islands (Sardinia and Sicily) and mainland. General comment for all projects: the scope of TYNDP project analysis is broader than national. This was done in line with TYNDP 2020 and the possibility of de-clustering projects will be considered in the future. | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | True |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Increase market exchanges between market zones Increase of security of supply increase RES integration |  |  | Italian northern border Internal (Italy) Internal (Italy) | 500-1000 1000 1000 | 500-1000 1000 1000
340 | Avelgem-Courcelles (Boucle du Hainaut): new corridor | The development of ~6 GW transport capacity through the elaboration of a new corridor between Avelgem and Courcelles.This corridor is envisioned to be implemented in AC technology. Timing, routing, scope, etc. subject to feasibility studies and subsequent spatial planning procedures. Today, the west and the center of the country are connected on 380 kV via only one corridor between Mercator and Horta in HTLS. Additional capacity between the west and the center is, however, required to sustain price convergence within a European merit order increasingly characterized by RES. A new corridor Avelgem-Courcelles would deliver around 6 GW of capacity and at the same time increases the maintainability and reliability of the grid, fulfilling the regulatory expectation that internal grids should be sufficiently strong so that society can fully reap the benefits from European market integration. Avelgem–Courcelles corridor is a prerequisite for the integration of new offshore & onshore production capacity west of Mercator and for integration of a second interconnector with Great-Britain (Nautilus). | Elia | BE | NDP1, Belgium, 2020-2030, §4.1.4, page 10 https://www.elia.be/-/media/project/elia/elia-site/infra-and-projects/investment-plans/federal-development-plan-2020-2030/fr/20190516_plan-de-developpement-federal_fr.pdf | 2029 | 3 | False | True | New | False |  |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | More information about the project can be found following these links: - Project site: https://www.elia.be/en/infrastructure-and-projects/infrastructure-projects/boucle-du-hainaut - National Development Plan: https://www.elia.be/-/media/project/elia/elia-site/infra-and-projects/investment-plans/federal-development-plan-2020-2030/nl/20190516_federaal-ontwikkelingsplan_nl.pdf?la=en | Infrastructure to reduce price differentials between EU and/or non-EU countries Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project deals with future more frequently expected situations with coinciding imports from France and UK together with evacuation of offshore wind. This project contributes to sustain price convergence between regions. Increased redundancy of onshore path ways will put less restrictions on cross border transmissions capacity for the market. This projects foresees the installation of phase shifting transformers enabling power flow control and optimizing the use of existing infrastructure. This project contributes to resolving internal congestions, considering expected high international flows as well as internal grid flows due to increased market exchanges. This project creates the necessary onshore grid capacity to facilitate offshore wind development. This project will facilitate further offshore development and create grid hosting capacity for onshore and offshore RES development. |  |  | Internal (Belgium) | 6000 | 6000
341 | North CSE Corridor | This project will consist of three investments. The investments of this project are SS 400/110 Belgrade 50, OHL 400 kV SS Belgrade 50 - WPP Cibuk and doubling existing OHL 400 kV Portile de Fier (RO) - Djerdap 1 (RS). Every investment included in this project represents a segment of the new significant corridor in the East-to-West direction, boasting the massive cross-border impact on the boundary between Serbia and Romania. This, in detail, means that the project will enhance the market integration in the region, allowing the lower difference in marginal energy costs, allow the connection of huge capacities of renewable sources that have applied for connection in the observed area (only in Serbia, there is over 3 GW of new wind and solar power plants foreseen in the Banat region) and affect the security of supply in the aforementioned region by increasing the available balancing capacity across the mentioned border. It is clear that the new renewable capacities, enabled for connection by this project's commissioning, will enormously change the generation mix in Serbia and provide a boost for the Serbian transition towards the sustainable and environmentally acceptable green energy production. | EMS, Transelectrica | RO ;RS | Plan razvoja prenosnog sistema Republike Srbije za period 2020 - 2029, page 122 (Serbian national TYNDP 2020-2029) - available at: http://www.ems.rs/media/uploads/Plan-razvoja-prenosnog-sistema-Republike-Srbije-2020-2029.pdf. Plan de Dezvoltare RET 2022-2031 (Transelectrica development plan 2022-2031), submitted in May 2022 for approval to the Romanian NRA- available at: https://www.transelectrica.ro | 2029 | 2 | True | False | MostlyNew | False |  | These investments will help the evacuation of RES in North-East part of Serbia and enhance energy exchange in the East-West corridor. | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | True | http://ems.rs/media/uploads/Plan_razvoja_prenosnog_sistema_2.pdf | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | As the project contributes to the increase of the transfer capacity across the border between Serbia (non-EU) and Romania (EU), it is safe to claim that it will enhance the market integration in the region and reduce the price differentials, as requested by this The internal investments in Serbia, included in the scope of North CSE Corridor, are foreseen to mitigate the risks of potential blackouts in the Belgrade region. Investment SS Belgrade West will provide major help in reducing the loading of the existing 400/x and 220/x kV substations in Srem area. Due to the fact that the commissioning of this project creates an additional energy corridor between Serbia and Romania, as confirmed by the NTC calculations, it can be claimed that it will, among other benefits, prove to be a major asset in the balancing flexibility area for both sides. As the Banat region in the close proximity of the border between Serbia and Romania offers a great possibility for the connection of renewable sources, the investments enveloped by this project will most certainly help the safe and reliable evacuation of the produced energy to the systems of interest. | Romania - Serbia - 844 | Romania - Serbia - 1524 - | Romania - Serbia | 680 | 720 | What should be underlined for this project is that it is also a precondition for the integration of around 3 GW of installed capacity of renewable energy sources in Southern Banat area, making it nearly irreplaceable for the green transition towards the sustainable generation in the affected systems.
342 | Central Balkan Corridor | This corridor will enable transmission of energy from east to west on the border between Bulgaria to Serbia and further to Montenegro and Bosnia and Herzegovina. It consists of several investments from SS Sofia West on the east to SS Pljevlja 2 and SS Visegrad on the west. In that way this corridor will be directly connected with project Transbalkan corridor (therefore, enabling the connection between Bulgarian energy market and Italian energy market), which represent a direct prerequisite for the proper development of the Central Balkan corridor. Among the numerous other benefits expected once this project is commissioned, the increase of NTCs on the borders between the involved countries (implying both the market integration and additional resources in securing the reliability of transmission systems' operation) can be seen as one of the most prominent. This project could also prove to be a strong asset in fully utilizing the hydro potentials of Western Serbia. | JSC EMS, ESO EAD, CGES, NOS BiH | BA ;BG ;ME ;RS | Plan razvoja prenosnog sistema Republike Srbije za period 2020 - 2029, page 123, (Serbian national TYNDP 2020-2030); URL: http://www.ems.rs/media/uploads/Plan-razvoja-prenosnog-sistema-Republike-Srbije-2020-2029.pdf | 2034 | 2 | True | False | MostlyUpgrade | False |  | These investments will form a new 400 kV corridor from Bulgaria, through Serbia to the border with the Bosnia and Herzegovina and Montenegro. New corridor will enable evacuation of energy from new RES in Bulgaria to the western part of Balkan region. | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | True | http://ems.rs/media/uploads/Plan_razvoja_prenosnog_sistema_2.pdf | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The Central Balkan corridor, among other investments, also includes strengthening of the interconnections in the CSE region (that involves both EU (Bulgaria) and non-EU countries), enhancing the market integration in the area of interest and, hence, succeeding in reducing the price differentials. As the project envelops the replacement of severely ageing 220 kV infrastructure in Central Serbia with the new 400 kV lines and substations, it is expected to significantly improve the system reliability in this area, thus reducing the possibility of putting the security of supply at risk in some operational regimes. Since the project of Central Balkan corridor offers the new interconnections between Serbia and several neighboring countries, it is most certainly envisaged as valuable improvement regarding the system flexibility, the full impact of which becoming apparent in the light of rapidly developing renewable energy sources in the CSE region. This project affect the RES integration in a manner similar to one relevant for the Project 227 (Transbalkan Corridor), focusing, among other benefits, on strengthening the lines in Western Serbia, near the Drina river, offering great potential for the energy production in the hydro plant capacities. | Montenegro - Serbia - 840 Bosnia-Herzegovina - Serbia - 2310 Bulgaria - Serbia - 1490 | Montenegro - Serbia - 840 - Bosnia-Herzegovina - Serbia - 1200 - Bulgaria - Serbia - 1490 - | Montenegro - Serbia Bosnia Herzegovina - Serbia Bulgaria - Serbia | 160 1180 490 | 410 490 270
343 | CSE1 New | The project will contribute in strengthen Croatian transmission grid along its main north-south axis (in parallel with eastern Adriatic coast) allowing for additional long-distance power transfers (including cross border) from existing and new planned power plants (RES/wind/ and conventional/hydro and thermal/) in Croatia (coastal parts) and BiH to major consumption areas in Italy (through Slovenia) and north Croatia. The increased transfer capacity will support market integration (particularly between Croatia and Bosnia-Herzegovina) by improving security of supply (also for emergency situations), achieving higher diversity of supply & generation sources and routes, increasing resilience and flexibility of the transmission network. | HOPS, NOS-BIH | BA ;HR | Desetogodišnji plan razvoja hrvatske prijenosne mreže 2021.-2030. s detaljnom razradom za početno trogodišnje i jednogodišnje razdoblje, Croatia, 2021, Page 88, Page 118 | 2033 | 2 | True | False | New | False |  | The Project implies increasing of transfer capacity between HR and BA by construction of new SS 400/110 kV Lika and its connection to an existing SS 400/220/110 kV Melina and SS 400/220/110 kV Konjsko in HR, and to an existing SS 400/110 kV Banja Luka in BA. | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | True |  |  |  | Bosnia-Herzegovina - Croatia - 500 | Bosnia-Herzegovina - Croatia - 1000 - Croatia - - <1000 | Croatia - Bosnia and Herzegovina | 644 | 298
346 | ZuidWest380 NL Oost | New 380 kV connection between Rilland and Tilburg including new substation. | TenneT-NL | BE ;NL | Investeringsplan net op land 2020-2029, The Netherlands, page 50, https://www.tennet.eu/fileadmin/user_upload/Company/Publications/Investeringsplannen/IP2020_NOL_201001.pdf | 2029 | 3 | False | True | New | False |  |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | True | http://www.zuid-west380kv.nl/ (in Dutch) | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Upgrade of the internal grid helps increase the cross-border exchange capabilities Netherlands and Belgium reducing thus price differentials between these different bidding zones Due to the change of the generation mix in both countries as well as the need to increase the interconnection capacity between the two countries, a new pattern of power flows will be created. This project, in combination with projects 262 and 297, helps facilitate these new needs and flow patterns By upgrading existing parts of the transmission grid, but also creating new corridors in it, a cost-efficient integration of large amounts of offshore wind production is implemented and thus reduces possible RES curtailment. | Belgium - The Netherlands - 1000 | Belgium - The Netherlands - 1000 - Belgium - - <1000 The Netherlands - - 1000 - 5000 | Belgium - Netherlands | 1000 | 1000
349 | MaresConnect | MaresConnect is a 750MW HVDC, subsea power interconnector between Ireland (Maynooth) and Wales (Bodelwyddan). MaresConnect will consist of two converter stations – one located close to the Maynooth 220kV substation west of Dublin and the other close to the Bodelwyddan 400kV substation in Denbighshire – connected by two High Voltage Direct Current cables under the Irish Sea.The cable route passes underground from Bodelwyddan to the coast and heads west under the seabed across the Irish Sea to landfall near Dublin Bay and continues underground to Maynooth in west Dublin. | Mares Interconnector Holdings Limited | GB ;IE | Project Ireland 2040 National Development Plan 2021-2030.: Page 37, 127, The reliability of electricity supplies will be strengthened through investment in the electricity transmission and distribution grid and through further interconnection with other electricity markets, including the Celtic Interconnector to France and further interconnection to the UK. The Project is included in All-Island Generation Capacity Statement 2021-2030 . "In Ireland, there is a further interconnector project (MARES Connect) from Ireland to GB, it is part of a wider project that includes a sea water pumped hydro station" (please note the current project excludes the pumped hydro station and is point to point interconnector only. The Project is included in National Grid's Interconnector register https://www.nationalgrideso.com/industry-information/connections/reports-and-registers | 2027 | 1 | True | False | New | False |  | MaresConnect is composed of an HVDC system which shall link the electricity grids of Ireland and Great Britain via submarine cables running between converter stations in Ireland and Wales. It is a High Voltage Direct Current (HVDC) connection capable of providing capacity of 750 MW, flowing in both directions (import / export). This system shall consist of convertor stations at Bodelwyddan in Wales and Maynooth in the Greater Dublin area, linked by a HVDC submarine cable. At each of these locations there is an interface with the TSO’s 245kV or 400kV AC network with associated infrastructure including connection bays . | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | False | Please see our website at www.maresconnect.ie | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) | Irish wholesale electricty prices are increasingly correlated to climatic conditions. High wind days see lower prices than the UK and low wind days generally see higher prices. MaresConnect will lead to a convergence of pricing through import/export between the two countries Under EirGrid energy scenarios the minimum target levels of interconnection would rise by 2030 to 2.8GW for the 15% Interconnection Target and 3.6GW for the 30% Installed RES Target. Ireland requires MaresConnect to achieve the 15% Target. The 30% RES target is not achieved even with the addition of MaresConnect. DECC considers RES curtailment as a high priority and highlighted the issue to the EU as part of its presentation on the PCI list in Brussels in February 2021. DECC’s policy is to identify interconnector (including MaresConnect) and storage projects that can address system operational issues Ireland’s already high penetration of renewables on its network will increase to close to 90% SNSP. Further infrastructure development will be required in the form of batteries and interconnector capacity to allow EirGrid to adequately manage voltage stability. | Great-Britain - Ireland - 1450 | Great-Britain - Ireland - 1954 - Ireland - - 1000 - 5000 | Ireland- United Kingdom | 750 | 750
350 | South Balkan Corridor | This project consists of two investments: 400 kV OHL Bitola(MK)- Elbasan(AL) and 400/110 kV SS Ohrid, in Macedonia. The interconnection contributes to increasing the transmission capacity in the East-West direction. The mentioned SS will increase the security of supply in the SouthWest part of the FYR of Macedonia. Construction of 400 kV OHTL interconnection from SS Bitola 2 to Macedonian/Albanian border and SS 400/110 kV Ohrid 400 kV interconnection transmission line Bitola (Macedonia) - Elbasan (Albania) is the last part of the implementation of the Corridor 8 in the context of creating a corridor East-West power transmission corridor between Bulgaria, Macedonia, Albania and Italy. | MEPSO | AL ;MK | 2020 | 2023 | 4 | True | False | New | False |  | The construction of the 1623:investment (SS Ohrid) will enable the connection of the investment (1622) interconnection Bitola - Elbasan, will improve the voltage conditions in the southwestern part of Macedonia and will provide security of supply. | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | https://author.energy-community.org/enc-author-prd/enc/regionalinitiatives/infrastructure/PLIMA/EL13.html https://www.mepso.com.mk/index.php/en/bit-elb-en/ | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) | This project is part of strengthening the energy transmission corridor from east to west. Further connecting of the Balkan countries with Italy will contribute to reducing the price difference between EU and non EU countries. By building a new substation, 400/110 kV SS in the Ohrid region, security of supply and voltage stability will be improved in the southwest of the country. |  | Albania - Greece - 1000 - Greece - North Macedonia - 1000 - | Albania - North Macedonia | 500 | 500
375 | Lienz (AT) - Veneto region (IT) 220 kV | Reconstruction of the existing 220kV-interconnection line between Lienz and Veneto Region (IT). The project includes the adjustment of power regulation devices. Due to an update of the list of cross-border projects interconnecting Italy with other Member States within 2020, the 2020 interconnection ratio of Italy has been updated accordingly (from previous value of 9% computed by ENTSO-E in TYNDP 2018 to roughly 8%). As the Interconnection level of 10% will not be reached by 2020, Italy is requested to investigate options of further interconnections. | Austrian Power Grid, Terna | AT ;IT | Piano di Sviluppo 2021 – Avanzamento Piani di Sviluppo Precedenti – Avanzamento Nord Est https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete/page n.96, Italy; | 2035 | 2 | True | False | Upgrade | False |  |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | True | Italian Development Plan: http://www.terna.it/it-it/sistemaelettrico/pianodisviluppodellarete/pianidisviluppo.aspx Austrian: National development plan: http://www.apg.at/en/netz/netzausbau/Netzentwicklungsplan | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project contributes to lower the price differentials between Italy North and Austria market area. This project will contribute to reduce system adequacy deficiencies by increasing transmission capacity. This project helps Italy to reach the 15% interconnection target by 2030. This project will improve the integration of italian RES generation. | Austria - Italy - 500 | Austria - Italy - 1000 - Austria - - <1000 Italy - - 1000 - 5000 | Austria - Italy | 500 | 500
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | The project aims at the reconductoring of the already existing 400kV interconnection line between Meliti (GR) and Bitola (MK), in order to increase transfer capacity between the power systems of Greece and North Macedonia. | Admie, MEPSO | GR ;MK |  | 2035 | 1 | True | False | Upgrade | False |  |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | False |  | Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) | Project implementation will contribute to a further improvement of the following ITEG indicators: 2. pushing ratio between nominal transmission capacity and installed RES capacity past 30% In both 2030 & 2040 horizon, the TYNDP 2022 System needs study indicates opportunity for increasing the cross-border capacity on the GR-MK border. The project, as an upgrade of the existing Meliti(GR)-Bitola(MK) interconnector, will provide balancing flexibility to the Greek and North Macedonian power systems. | Greece - North Macedonia - 500 | Greece - North Macedonia - 1000 - | Greece-North Macedonia | 500 | 500
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | This study envisions an upgrade of the existing interconnector VanEyck-Maasbracht between Belgium and the Netherlands making use of PSTs and/or HTLS technology.The study will determine the appropriate implementation option and timing, taking into account - The already planned upgrade of the Zandvliet-Rilland interconnector on the BE-NL border (see project 262) - The synchronisation with developments in the NL-DE border Project motivation: A need has been identified to further develop interconnection capacity on the BE-NL border, hereby alleviating VanEyck-Maasbracht as bottleneck. This project effectively increases the degree of interconnectivity between the Belgian and Dutch bidding zone. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. This project is likely to increase the potential for imbalance netting & reserve sharing due to increased remaining available margins of the cross border transmission capacity. PSTs will also help to balance the flows over the different cross border lines of the Belgian Dutch interconnection. | Elia, TenneT-NL | BE ;NL | NDP1, Belgium, 2020-2030, §4.2.3.1, https://www.elia.be/-/media/project/elia/elia-site/infra-and-projects/investment-plans/federal-development-plan-2020-2030/fr/20190516_plan-de-developpement-federal_fr.pdf | 2032 | 1 | True | False | Upgrade | False |  |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | False | True | More information about the project can be found following this link: - National Development Plan: https://www.elia.be/-/media/project/elia/elia-site/infra-and-projects/investment-plans/federal-development-plan-2020-2030/nl/20190516_federaal-ontwikkelingsplan_nl.pdf?la=en | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between the Belgian and Dutch bidding zones. The possibility of higher market exchanges between these two bidding zones leads to a higher price convergence in more hours of the year and reduces therefore the price differentials. This project has an important adequacy contribution due to decreasing figures of installed conventionals (bad market conditions) and considering the nuclear phaseout in Belgium. Phase shifting transformers will help to balance the flows over the different cross border lines of the Belgian Dutch border. RES integration implies higher flows in the meshed AC-grid and thus increases the need for cross border transmission capacity. This project satisfies this need in a cost-efficient manner. | Belgium - The Netherlands - 1000 | Belgium - The Netherlands - 1000 - Belgium - - <1000 The Netherlands - - 1000 - 5000 | Belgium - Netherlands | 1000 | 1000
378 | Transformer Gatica | New tranformer 400/220 kV in existing Gatica subestation, with potential impact in cross border values | Red Eléctrica | ES | Spanish NDP, "Plan de desarrollo de la red de transporte de energía eléctrica.Horizonte 2021-2026" Project Label INT_ESP-FRA_2: Refuerzos interconexión España-Francia (Gatica) pg279 | 2027 | 2 | False | True | New | False |  |  | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | https://www.planificacionelectrica.es/proyectos ;project label INT_ESP-FRA_2: Refuerzos interconexión España-Francia (Gatica) |  |  |  |  | Internal (Spain) | - | -
379 | Uprate Gatica lines | Uprate of the following 400kV lines that reach Gatica subestation : Gatica-Gueñes, Gatica-Amorebieta-Ichaso and Gatica-Azpeitia. This internal project has influence in the exchange capacity values between France and Spain, and it is directly related to the P16 Biscay Gulf. | Red Eléctrica | ES | Spanish NDP, "Plan de desarrollo de la red de transporte de energía eléctrica.Horizonte 2021-2026" Project Label INT_ESP-FRA_2: Refuerzos interconexión España-Francia (Gatica) pg279 | 2026 | 2 | False | True | Upgrade | False |  | The uprate to increase the capacity of the 3 400kV lines connected to the Gatica subestation are clustered as they serve for the same purpose and have overloads in case of failure of any of them, when the new project HVDC ES-FR is commissioned and connected to the Gatica subestation | TYNDP 2018 ;TYNDP 2020 ;TYNDP 2022 | True | True | https://www.planificacionelectrica.es/proyectos ;project label INT_ESP-FRA_2: Refuerzos interconexión España-Francia (Gatica) |  |  |  |  | Internal (Spain) | - | -
1034 | HVDC corridor from Northern Germany to Western Germany | Project 1034 consists of two new HVDC cable from Heide/West to Polsum and from Wilhelmshaven to Region Hamm. The HVDC have a transfer capacity of 2 GW each. The project is a grid expansion project for low-loss transmission of high power over long distances from Northern Germany to the Ruhr-Area. Northern Germany is characterized by a large number of regenerative onshore and offshore energy sources which exceed the demand of Northern German loads. The Ruhr-Area, however, is a high-production region with large conventional generation capacity that has to be substituted by renewable generation capacity due to the German coal phase-out. | Amprion | DE | NDP, Germany, Netzentwicklungsplan 2035 Version 2021, Project DC21 and DC25, p. 409 | 2031 | 2 | False | True | New | True | 2.31.2 and 2.31.3 | missing | TYNDP 2020 ;TYNDP 2022 | False | True | 5th PCI-List: https://ec.europa.eu/energy/sites/default/files/fifth_pci_list_19_november_2021_annex.pdf The project was part of the previous TYNDP 2020, Link to the Website: https://tyndp2020-project-platform.azurewebsites.net/projectsheets/transmission/1034 Further information of the project, its investments and their necessity particularly for the German Energiewende can be found in the German grid development plan (mostly in German): http://www.netzentwicklungsplan.de/en/front |  |  |  |  | Germany - Denmark (West) Germany - The Netherlands Internal (Germany) | 0 2950 4000 | 650 300 4000
1039 | SE North-south long-term reinforcements | Replacement and upgrading of ageing overhead lines and reactive measures in substations and series compensations in order to increase capacity between SE2 and SE3. | Svenska Kraftnät | SE | 10-Year Grid Investment Plan 2020-2029 , Sweden, 2020, p. 12. {Available online: https://www.svk.se/siteassets/om-oss/rapporter/2020/10-year-development-plan-2020-2029.pdf} | 2040 | 1 | False | True | MostlyUpgrade | False |  | There are two parallel lines under consideration. | TYNDP 2020 ;TYNDP 2022 | False | False | Svenska kraftnät has published a national development plan in 2019. The purpose of the plan is to be an investment plan for the following ten years, 2020-2029. The investment plan presents a detailed look of the projects Svenska kraftnät intends to realize under the stated time period. The plan is available in Swedish through the following link: https://www.svk.se/siteassets/om-oss/rapporter/2019/systemutvecklingsplan2020-2029.pdf (Swedish) | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) | Add 1000 MW extra transfer capacity among Swedish price zones. Replacement and upgrading of ageing overhead lines in order to increase capacity between SE2 and SE3. Replacement and upgrading of reactive measures in substations and series compensations in order to increase voltage stability. |  |  | Internal (Sweden) | 1000 | 1000
1040 | LirIC | LirIC is a new HVDC sub-sea interconnector between Scotland and Northern Ireland. LirIC is being developed to increase the level of interconnection between Scotland and Northern Ireland addressing a market need and resulting in welfare generation opportunities in GB and consumer benefit in Ireland. A second beneficial driver for the project is the alleviation of Ireland's synchronous generation constraint, where there is an imposed limit on the level of demand that can be met by wind. These two effects result in significant benefit for British exports to Ireland to exploit wholesale power price arbitrage and Irish exports to Britain to avoid wind curtailment. | Transmission Investment | GB | No, however concept positively evaluated in NGESO Network Options Assessment, chapter 6, page 86 - see ref below | 2028 | 1 | False | True | New | False |  | N/A - No clustering | TYNDP 2020 ;TYNDP 2022 | False | False |  |  |  | Great-Britain - Island of Ireland - 1450 | Great-Britain - Island of Ireland - 1954 - Island of Ireland - - 1000 - 5000 | Internal (United Kingdom) | 700 | 700
1041 | GREGY Green Energy Interconnector | GREGY Interconnector concerns the possibility to create a new energy highway within the Mediterranean Basin, by interconnecting Egypt and Greece. GREGY project consists of an HVDC interconnection from Wadi-El-Natroon (Egypt) to Attica area (Greece) of about 1472 km total length. GREGY will supply renewable power on a permanent basis (8760 h) up to the capacity of 3000MW. The project will exploit part of the 61 GW RES capacity that will be installed in Egypt by 2035 according to the long-term Egyptian Development Plan. GREGY will allow 100% RES energy exports, contractually ensured by bespoke Power Purchasing Agreements (PPAs), from Egypt to Greece, and vice versa, at times of high-RES generation, contributing to a significant increase of participation of RES in the energy mix and reduction of greenhouse emissions of the power sector. In addition to RES increase, benefits such as market coupling, enhanced security of supply (Adequacy, Flexibility, Stability) and socio-economic welfare are enabled through GREGY establishing a new interconnection between two large synchronous areas. | ELICA INTERCONNECTOR SINGLE-MEMBER S.A. | EG ;GR | No | 2028 | 1 | True | False | New | False |  |  | TYNDP 2020 ;TYNDP 2022 | False | False |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | GREGY establishes a high capacity connection route between southeast Europe and Egypt along with nearby power systems, enabling electricity trading. Therefore, it will constitute a critical asset towards coupling of power markets of EU with North Africa and the Middle East. Higher transmission capacity will be necessary to accommodate new flows due to higher RES penetration. GREGY can contribute with releasing capacity (503-730 MW/h) at the borders of Greece with Bulgaria and Italy, in addition to the bi-directional power flow between Egypt and Greece. GREGY interconnector will enable access to new balancing sources for both Greek and Egyptian power systems. The high capacity of GREGY will permit trading of significant volumes of balancing and reserve services, increase flexibility and allow optimal operation of variable RES. Implementation of GREGY transferring 100% RES (which can be 1) consumed in Greece, 2) used for producing green H2, 3) transferred to Europe) shall lead to significant reduction of RES curtailment. Such green energy will be secured by long-term PPAs with RES producers in Egypt. |  |  | Greece - Egypt | 3000 | 3000
1042 | Offshore Wind LT 1 | The aim of the project is to integrate 700 MW off-shore wind farms in Baltic Sea near Lithuania coast. Onshore connection to 330 kV Darbenai substation. Studies are in progress concerning environmental assessment and maritime planning. | Litgrid AB | LT | "Development plan of the electric power system and transmission grid. 2021-2030" (https://www.litgrid.eu/uploads/files/dir580/dir29/dir1/10_0.php), June 2021, pages 23, 26. | 2028 | 2 | False | True | New | False |  |  | TYNDP 2020 ;TYNDP 2022 | False | True |  | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) Infrastructure to connect energy intensive industry to electricity network (e.g. data hubs,…) | Generation from offshore wind will increase system adequacy for Lithuania. New offshore wind farms will provide sufficient electricity meeting demand increase (electrification of transport sector, P2H, electrolysers). New offshore wind farms will ensure decarbonization of energy intensive industry (green hydrogen for industry). |  |  | Internal (Lithuania) | 700 | 700
1046 | Finnish North-South reinforcement | This project consists of several 400 kV overhead lines built in the north-south direction inside Finland (+other required investments to achieve the full capacity). The project is built to increase the North-South transmission capacity thus enabling the integration of new renewable generation in northern Finland and transfer of power to the consumption centers in the south. | Fingrid | FI | Kantaverkon kehittämissuunnitelma 2022-2031, available here: https://www.fingrid.fi/kantaverkko/kehittaminen/kantaverkon-kehittamissuunnitelma/kantaverkon-kehittamissuunnitelma-2022-2031/ (currently in Finnish, will be available in English later). The project consits of various investments mentioned in the development plan. | 2030 | 2 | False | True | New | False |  |  | TYNDP 2020 ;TYNDP 2022 | False | False | Fingrid has published a national development plan in 2022-2031. The investment plan presents a detailed look of the projects. The plan is available in Finnish: https://www.fingrid.fi/kantaverkko/kehittaminen/kantaverkon-kehittamissuunnitelma/kantaverkon-kehittamissuunnitelma-2022-2031/ (will be available in English later) The concept of reinforcing the north south direction in Finland is discussed for example in Fingrid's network vision: https://www.fingrid.fi/globalassets/dokumentit/fi/kantaverkko/kantaverkon-kehittaminen/fingrid_network_vision.pdf | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) Infrastructure to connect energy intensive industry to electricity network (e.g. data hubs,…) | Enables Finland to provide full cross border capacity to Swedish and Estonian borders and thus reduces the price differentials between EU countries. Increases the capability to transmit wind power from the northern and western parts to the southern parts of Finland. Supports the Finnish carbon neutrality goal 2035 by allowing the replacement of natural gas, coal and oil with clean electricity. Supports the Finnish carbon neutrality goal 2035 by allowing the replacement of natural gas, coal and oil with clean electricity, including fossil free steel, data centers, battery manufacturing and hydrogen. |  |  | Internal (Finland) | 3000 | 3000
1047 | Emden-Eemshaven | Increase of the interconnection capacity between the Netherlands (Eemshaven) and Germany (Emden) by adding a new 380kV tranmission line. The project is planned as a combination of overheadline, onshore cable and sub sea cable. | TenneT DE | DE ;NL |  | 2035 | 1 | True | False | New | False |  |  | TYNDP 2020 ;TYNDP 2022 | False | False |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | contributes to reduction of price spread by 2040 increases system size, thus facilitates sharing of ancillary service high RES increase expected on both sides of the border |  | Germany - The Netherlands - 1000 - Germany - - 5000 - 10000 The Netherlands - - 1000 - 5000 | Germany - Netherlands | 1000 | 1000
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | The project refers to the construction of a submarine DC transmission link of total capacity 2000MW (2x1000MW) interconnecting Egypt's North Mediterranean coast and Greece at the island of Crete. A new HVDC conversion station close to the existing thermal power plant of Atherinolakkos in South-East Crete will be the connection point to Greece. Crete interconnection with mainland Greece is already under way by the Greek TSO (IPTO) with the implementation works expected to be completed before 2030 (both AC and DC links). Moreover, the "Southern Aegean Interconnector" project will provide another transmission route of the transfer capacity through the Aegean sea. The connection point in Egypt will be at its Northern coast located South of Crete, where the bulk of Egypt's electrical load and HV transmission grid infrastructure is located. All the aforementioned installations (converter stations, substations etc) will be of closed type using GIS technology. The proposed Greece - Africa interconnection project will provide energy stability to the Eastern Mediterranean Sea area as intercontinental energy transfers will be facilitated and generation adequacy of the region will be increased. | Greece Africa Power Interconnector SMSA (Member of Eunice Energy Group) | EG ;GR |  | 2028 | 1 | True | False | New | False |  |  | TYNDP 2020 ;TYNDP 2022 | False | False | https://eunice-group.com/projects/greece-africa-power-interconnector-gap-interconnector/ | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. | Energy flows between Greece and Egypt that will be achieved through GAP Interconnector (HVDC cable) will lead to reduced price differentials between EU (Greece) and non-EU countries (Egypt). The proposed Greece - Africa interconnection project will provide energy stability to the Eastern Mediterranean Region as intercontinental energy transfers will be facilitated and generation adequacy of the region will be increased. Various future scenarios will be made eligible for testing and analysis between EU and non EU cross border flows. Certainly the increased interconnection capacity between Greece and Egypt provided via the development of GAP Interconnector shall lead to signifcant decrease of RES curtailments and will further enable the development of RES. The increased Interconnection capacity provided via the infrastructure of GAP Interconnector will enhance System Adequacy for both Power Systems (Greek - EU and Egyptian - Africa). Power failures will be mitigated in a more bulk interconnected grid. |  |  | Greece - Egypt | 2000 | 2000
1049 | Cronos Energy Ltd | Cronos Energy Ltd (“Cronos”) is developing a 1400MW DC Bipole VSC interconnector between England and Belgium with the financial support of one of Europe's largest infrastructure funds. The management team of Cronos has a successful track record in developing and delivering interconnectors and transmission projects as well as large-scale grid connected power stations in the UK and Europe and has been involved in over 40GW of transmission power station and interconnector projects in Europe. Our mandated technical advisor is WSP Ltd. Legally binding connection and construction agreements have been entered into for the Cronos Interconnector and the project will apply for a UK cap & floor regulatory regime for 50% of the project costs in the Third Window in 2022 from the NRA with the other 50% of the project under a Belgian cap & floor regime yet to be applied for. The Project will operate under applicable EU Regulations, including Regulation (EU) 2015/1222 and multi-region loose volume coupling (once implemented). Cronos and its investors are committed to the Project and have all required resources to deliver it. | Cronos Energy Ltd | BE ;GB |  | 2029 | 1 | True | False | New | False |  |  | TYNDP 2020 ;TYNDP 2022 | False | False | Cronos Energy Ltd is happy to provide any further info requested | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The Project will connect the GB and BE electricity markets which have different wholesale electricity prices. The electricity flow will be dictated by the difference in the electricity price between those markets (flowing to the higher priced market) reducing he price differential between these countries. The interconnector will allow GB more access to the entire BE electricity generation mix and vice versa. In turn, this increases security of supply, system capacity margin and load factors to maximise output and reliability and minimise the risk of power failures The Project helps system operators at both ends as it can ramp quickly in response to rapid changes in supply and demand being especially useful in the balancing markets. Responding quickly to price signals at times of system stress is an important tool in managing volatility in different timeframes. The interconnector will reduce the cost and curtailment of renewable energy sources as both GB and BE are building much offshore wind that connects into the coast, and the onshore grid is being reinforced in both countries to maximise the efficiency of both interconnectors and offshore wind. | Belgium - UK - 1400 | Belgium - UK - 1400 - Belgium - - <1000 | Belgium - United Kingdom | 1400 | 1400
1050 | Tarchon Energy Ltd | Tarchon Energy Ltd (“Tarchon”) is developing a 1400MW DC Bipole VSC interconnector between England and Germany with the financial support of one of Europe's largest infrastructure funds. The management team of Tarchon has a successful track record in developing and delivering interconnectors and transmission projects as well as large-scale grid connected power stations in the UK and Europe and has been involved in over 40GW of transmission power station and interconnector projects in Europe. Our mandated technical advisor is WSP Ltd. Legally binding connection and construction agreements have been entered into for the Tarchon Interconnector and the project will apply for a UK cap & floor regulatory regime for 50% of the project costs in the Third Window in 2022 from the NRA with the other 50% of the project being regulated under German requirements. The Project will operate under applicable EU Regulations, including Regulation (EU) 2015/1222 and Regulation (EU) 2019/943 and EU Forward Capacity Allocation Guideline (Commission Regulation (EU) 2016/1719) and multi-region loose volume coupling (once implemented). Tarchon and its investors are committed to the Project and have all required resources to deliver it. | Tarchon Energy Ltd | DE ;GB |  | 2030 | 1 | True | False | New | False |  |  | TYNDP 2020 ;TYNDP 2022 | False | False | Tarchon Energy is happy to supply any further info requested | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The Project will connect the GB and DE electricity markets which have different wholesale electricity prices. The electricity flow will be dictated by the difference in the electricity price between those markets (flowing to the higher priced market) reducing he price differential between these countries. The interconnector will allow GB more access to the entire DE electricity generation mix and vice versa. In turn, this increases security of supply, system capacity margin and load factors to maximise output and reliability and minimise the risk of power failures The Project helps system operators at both ends as it can ramp quickly in response to rapid changes in supply and demand being especially useful in the balancing markets. Responding quickly to price signals at times of system stress is an important tool in managing volatility in different timeframes The interconnector will reduce the cost and curtailment of renewable energy sources as both GB and DE are building much offshore wind that connects into the coast, and the onshore grid is being reinforced in both countries to maximise the efficiency of both interconnectors and offshore wind. | Germany - UK - 1400 | Germany - UK - 2800 - Germany - - 5000 - 10000 | Germany - United Kingdom | 1400 | 1400
1051 | Aminth Energy Ltd | Aminth Energy Ltd (“Aminth”) is developing a 1400MW DC Bipole VSC interconnector between England and Denmark with the financial support of one of Europe's largest infrastructure funds. The management team of Aminth has a successful track record in developing and delivering interconnectors and transmission projects as well as large-scale grid connected power stations in the UK and Europe and has been involved in over 40GW of transmission power station and interconnector projects in Europe. Our mandated technical advisor is WSP Ltd. Legally binding connection and construction agreements have been entered into for the Aminth Interconnector and the project will apply for a UK cap & floor regulatory regime for 50% of the project costs in the Third Window in 2022 from the NRA with the other 50% of the project being regulated under Danish requirements. The Project will operate under applicable EU Regulations, including Regulation (EU) 2015/1222 and Regulation (EU) 2019/943 and EU Forward Capacity Allocation Guideline (Commission Regulation (EU) 2016/1719) and multi-region loose volume coupling (once implemented). Aminth and its investors are committed to the Project and have the required resources to deliver it. | Aminth Energy Ltd | DK ;GB |  | 2031 | 1 | True | False | New | False |  |  | TYNDP 2020 ;TYNDP 2022 | False | False | Aminth Energy Ltd is happy to supply any further info requested. We will provide updated further information as soon as we signed the legal agreements that vary the existing legally binding connection and construction contracts. | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The Project will connect the GB and Danish electricity markets which have different wholesale electricity prices. The electricity flow will be dictated by the difference in the electricity price between those markets (flowing to the higher priced market) reducing he price differential between these countries The interconnector will allow GB more access to the entire DK electricity generation mix and vice versa. In turn, this increases security of supply, system capacity margin and load factors to maximise output and reliability and minimise the risk of power failures. The Project helps system operators at both ends as it can ramp quickly in response to rapid changes in supply and demand being especially useful in the balancing markets. Responding quickly to price signals at times of system stress is an important tool in managing volatility in different timeframes. The interconnector will reduce the cost and curtailment of renewable energy sources as both GB and DK are building much offshore wind that connects into the coast, and the onshore grid is being reinforced in both countries to maximise the efficiency of both interconnectors and offshore wind. |  | Denmark - UK - 1400 - Denmark - - <1000 | Denmark - United Kingdom | 1400 | 1400
1052 | Lienz (AT) - Obersielach (AT) | The 380-kV-ring can be completed in Austria with the reinforcement of the Carinthia transmission grid. The advantages of a ring structure are only made possible by the project. Security of supply in Carinthia and Austria can be guaranteed in the long term. With the 380-kV-ring closure in the south, a redundant connection of the renewable energy feed-in centers in the east Austria (mainly wind and PV) and the load centers with the pumped storage power plants in the central Alpine region. The 380-kV-ring closure is essential for the grid integration of renewable energies and the Austrian Federal Government's climate and energy strategy, and its necessity will also be addressed in the Carinthian Government's 2018-2023 program. The project will also enable the development of additional transmission capacity to the neighboring countries | Austrian Power Grid | AT | APG Netzentwicklungsplan 2021, AT, 2021, 11-14, 55, https://www.apg.at/en/Stromnetz/Netzentwicklung | 2032 | 2 | False | True | MostlyUpgrade | True | 3.28 |  | TYNDP 2020 ;TYNDP 2022 | False | True | https://www.apg.at/en/Stromnetz/Netzentwicklung | Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Facilitation of capacities between RES and pump storages in Austria as well as optimisation of cross border flows. Enabling future developments (load/generation). Faclilitation and optimisation of pump storage connections in the western part of Austria and therefore increasing flexibility. Connecting RES with pump storages. | Austria - Slovenia - 1000 | Austria - Slovenia - 1500 - Austria - - <1000 | Austria - Slovenia | 1528 | 1084
1054 | Westtirol (AT) - Zell/Ziller (AT) | An Upgrade of the existing 220kV-line Westtirol (AT) - Zell-Ziller (AT) and the erection of an additional 220/380kV-transformer. | Austrian Power Grid | AT | APG Netzentwicklungsplan 2021, AT, 2021, 14-3, 62, https://www.apg.at/en/Stromnetz/Netzentwicklung | 2029 | 2 | False | True | MostlyUpgrade | True | 3.1.4 |  | TYNDP 2020 ;TYNDP 2022 | False | True | https://www.apg.at/en/Stromnetz/Netzentwicklung | Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) | Facilitation of capacities between RES and pump storages in Austria as well as optimisation of cross border flows. Enabling future developments (load/generation). Connecting RES with pump storages. Faclilitation and optimisation of pump storage connections in the western part of Austria and therefore increasing flexibility. | Austria - Germany - 3100 | Austria - Germany - 3100 - Austria - - <1000 Germany - - 5000 - 10000 | Austria - Germany | 816 | 1086
1055 | Interconnection of Crete to the Mainland System of Greece | Crete is the largest electrically non-interconnected island system in Greece, representing a particular case, due to large size, rapid growth, remote location and large RES potential. The project aims to increase security of supply and improve stability issues of the island by its interconnection to the mainland system. It is expected to contribute to the reduction of the operation of oil-fired units that currently supply the island and in the long run to allow their progressive decommissioning, thus contributing to the reduction of production variable costs and greenhouse gas emissions. It will allow the full exploitation of local RES potential. The project shall ensure a more reliable and cost-effective supply of electricity to the island. This interconnection will be implemented in two phases. In Phase I Crete will be connected to Peloponnese with a 150 kV AC double circuit submarine cable interconnector of 2x200 MVA nominal transfer capacity. In Phase II Crete will be connected to Attica with a bipolar submarine HVDC-VSC link of 2x500 MW capacity transfer. The project in total contributes in achieving the EU-wide targets and policy objectives set in the 2030 climate and energy framework. | Admie | GR | NDP2022-2031, Greece, 2021, pr. No 14.26 & 17.7, page 68, 91-99, 150, 152, https://www.admie.gr/sites/default/files/users/dssas/DPA%202022-2031/%CE%94%CE%A0%CE%91%202022-2031.pdf | 2024 | 4 | False | True | New | False |  | The final design and implementation of the whole project with its clustering into two Phases imposed by several reasons, technical, financial and environmental. The aim to ensure security of supply for the island is the main reason for undertaking the investment. The rapid increase of electricity demand in the island, along with the need for decommissioning of the local oil-fired generation units, in short term horizon, to comply to the environmental Directives IED 2010/75/ΕΕ (IED) and 2015/2193/ΕΕ (MCPD directive), gave a character of urgency. The advanced level of maturity of the subproject of Phase I in terms of studies (detailed engineering, routing, seabed studies, environmental studies), in terms of financing (acquisition of grants in the framework of NSRF 2014-2020 and loans by EIB), in terms of low risk implementation due to capacity of promoter and its experience by similar AC interconnection projects (Cyclades interconnection to HETS) led to proceed immediately. Thus, the implementation of the Phase I has been started. Regarding Phase II project, it took more time to reach maturity. Phase II is technically more complicated. The need for in depth studies and better organization of the project implementation led IPTO to proceed with Phase II after implementation of major parts of Phase I in order to successfully achieve the best results and obtain the objectives as security of supply, increase of RES penetration, reduction of CO2 emissions, reduction of PSOs, etc. | TYNDP 2020 ;TYNDP 2022 | True | True |  | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure designed to offer more supply options to isolated areas | Crete, being until recently the largest electrically non-interconnected island system in Greece, is characterized by high annual consumption and load peak. Adequacy issues have been recognized, as several generation units have to be decommissioned or replaced according to EU Directives. The completion of the project ensures the island The project will allow the full exploitation of local abundant RES potential, which are subject to limitations imposed by its former autonomous operation and completion of Phase II of the project. Crete, being until recently the largest electrically non-interconnected island system in Greece, operated in autonomous mode. The completion of Phase II of the project will increase security of supply and improve stability issues for the electric system of the island |  |  | Internal (Greece) | 800 | 800
1058 | HVDC Interconnector DE-CH | This concept project concerns an extension of German HVDC lines towards Switzerland via an addi-tional HVDC link. It pursues an ultimate goal to realise a new HVDC North-South corridor connecting the generation capacities in the North Sea area with the consumption centres in the Mediterranean sea region. | Swissgrid, TransnetBW | CH ;DE | The project is not included in the last available German National development plan 2035 Version 2021 (NEP), because it was elaborated earlier than the TYNDP. The project is expected to be assessed in the coming German NDP. | 2037 | 1 | True | False | New | False |  |  | TYNDP 2020 ;TYNDP 2022 | False | False | TransnetBW Study “Electricity Grid 2050”, p.47: https://www.transnetbw.de/de/stromnetz2050/content/TransnetBW_Study_ElecricityGrid2050_and_Summary.zip | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) | This project increases the degree of interconnectivity between Germany and Switzerland and possibility of higher market exchanges, which lead to higher price convergence. The further expansion of RES capacities in Germany, especially offshore wind, leads to increasing RES-curtailment in the coming decades. By increasing the transmission capacity between Germany and Switzerland, the alternative HVDC measure allows a higher German export in hours of high RES infeed. The full controllability of the HVDC link between Germany and Switzerland will contribute to the voltage stability and security of supply, which can significantly increase the flexibility of power systems in both countries. | Germany - Switzerland - 1550 | Germany - Switzerland - 1550 - Germany - - 5000 - 10000 Switzerland - - <1000 | Switzerland - Germany | 1000 | 1000
1059 | Southern Italy | New 400 kV lines in Campania and in Calabria, affecting existing 400 kV substation. The link will remove grid constraints and congestions due to the new renewable installed capacity. | Terna | IT | Piano di Sviluppo 2021 – Avanzamento Piani di Sviluppo Precedenti – Avanzamento Centro Sud https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete/page132 | 2028 | 3 | False | True | New | False |  | Both investments contribute to the increase of NTC between the South and Calabria for a total of 900 MW. General comment for all projects: the scope of TYNDP project analysis is broader than national. This was done in line with TYNDP 2020 and the possibility of de-clustering projects will be considered in the future. | TYNDP 2020 ;TYNDP 2022 | False | True |  | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | Increase of security of supply The new line will allow congestion reduction on the Central-Southern/Southern border, and the integration of the local renewable production. |  |  | Italian Northern border Internal (Italy) | 500-900 200 | 500-900 200
1066 | Bulgaria - Turkey | The project concerns the construction of a new AC 400kV interconnection Bulgaria - Turkey. The proposed interconnection line with a total length 150 km will connect Maritsa East 2 SS in Bulgaria and Vize Havza SS in Turkey. This project, together with the project for a new interconnection between Greece and Turkey, compose the project “East Balkan Corridor” that will contribute to increasing the cross -border transfer capacities between ENTSO-E countries and Turkey and address a system need, identified in ENTSO-E's System Needs study. The construction of the two interconnections will also improve the stability of the connection of a large electricity system such as the Turkish one to the unified electricity system of the countries of continental Europe. Furthermore the project will allow integration of more renewables to the grids, support the convergence of market price between the neighboring countries and thus will help the realization of clean energy package targets. | ESO | BG ;TR |  | 2036 | 1 | True | False | New | False |  |  | TYNDP 2020 ;TYNDP 2022 | False | False |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. | contributes in reducing high price differentials indicated between Turkey and Bulgaria in the future due to the generation shift, enabling lower and more balanced wholesale prices. Constraints (e.g. congestion) occur in future scenarios where high flows are exchanged between Bulgaria and Turkey with the current grid. The project contributes in transfer capacity increase, thus minimizing congestion at the BG – TR border. The project supports the development of infrastructure in the area for the connection of large RES capacities in the south-eastern part of Bulgaria. Project implementation will enhance transmission capacity between Bulgaria and Turkey and thus will contribute to a further improvement of the 2nd ITEG indicator pushing ratio between nominal transmission capacity and installed RES capacity past 30% | Bulgaria - Turkey - 2100 | Bulgaria - Turkey - 2100 - | Bulgaria-Turkey | 1100 | 700
1067 | New AC 400 kV interconnection line Greece - Turkey | The project concerns the construction of a new AC 400kV interconnection Greece - Turkey. The proposed interconnection line with a total length 130 km will connect Nea Santa SS in Greece and Babaeski SS in Turkey. This project, together with the project for a new interconnection between Bulgaria and Turkey, compose the project “East Balkan Corridor” that will contribute to the increase of the cross-border transfer capacities between ENTSO-E countries and Turkey and address a system need, identified in ENTSO-E's System Needs study. The construction of the two interconnections will also improve the stability of the connection of a large electricity system such as the Turkish one to the unified electricity system of the countries of continental Europe. Furthermore the project will allow integration of more renewables to the grids, support the convergence of market price between the neighboring countries and thus will help the realization of clean energy package targets. | Admie | GR ;TR |  | 2035 | 1 | True | False | New | False |  | The new 400 kV OHL Nea Santa - Filippi is a necessary reinforcement in Greece in order for the new interconnection line between Greece and Turkey to deliver its full potential. | TYNDP 2020 ;TYNDP 2022 | False | False |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) | The project contributes in reducing high price differentials indicated between Turkey and Greece in the future due to the generation shift, enabling lower and more balanced wholesale prices. Project implementation will enhance transmission capacity between Greece and Turkey and thus will contribute to a further improvement of the 2nd ITEG indicator pushing ratio between nominal transmission capacity and installed RES capacity past 30%. Constrains (e.g. congestions) occur in future scenarios where high flows are exchanged between Greece and Turkey with the current grid. The project contributes in transfer capacity increase, thus minimizing congestions at the GR – TR border. The project, as a new interconnector between Greece and Turkey, will provide balancing flexibility to the Greek and Turkish power systems. | Greece - Turkey - 1600 | Greece - Turkey - 1100 - | Greece-Turkey | 600 | 600
1068 | LaSGo Link | LaSGo Link is a new multi terminal HVDC sub-sea interconnector project linking Sweden, the Island of Gotland and Latvia. The project consists of two sections: a 700MW internal grid reinforcement between the Swedish mainland and the island of Gotland and a 500MW cross border connection between the island of Gotland and Latvia. LaSGo Link is being developed to increase grid capacity to Gotland and increase the level of cross border capacity in the Baltic Sea region. This will meet the current challenge of security of supply experienced in this region and therefore support industry and the further growth of wind power in the Gotland region. The cross border element of the project will provide further routes to market for generation thereby reducing internal grid congestion in Sweden and providing socio-economic benefit to both Sweden, Latvia and the interconnected markets in the Baltic Sea region. | Transmission Investment | LV ;SE | This project is not included in a NDP. | 2031 | 1 | True | False | New | True | 4.11 | The LaSGo Link project is a multi-terminal HVDC link with converter stations sited in Sweden, the island of Gotland and Latvia. The Sweden to island of Gotland section is an internal Swedish grid reinforcement project but is required to support the connection of the cross border element between the island of Gotland and Latvia. Equally the sizing of the Sweden to Gotland section is based on the requirement of the cross border section. These two sections are therefore mutually inclusive and must be realised as a single project to maximise the capital efficiency and socio-economic welfare of the project. | TYNDP 2020 ;TYNDP 2022 | False | False | NOTE BY THE PROMOTERS: Beyond the economic benefits of 500MW of cross border capacity between Sweden and Latvia, the mid-terminal located on the island of Gotland will replace the aging existing HVDC cable connection between the Swedish mainland and Gotland which is expected to come to end of life between 2030 and 2035. This internal grid reinforcement will support the connection of significantly more offshore wind expected to be greater than 1GW in the seas around the island. Furthermore, the project will mitigate current security of supply issues limiting the industrial expansion on the island with a decarbonised energy approach. One example of such is a cement factory that could, with an increase of clean energy supply, reduce their emmissions (that is today 5% of Sweden's total emmissions) towards zero. By improving the economic viability and expansion of local industry and creating further job opportunities on the project itself the project will secure and increase the number of jobs on Gotland, which is critical for the local development. The project will be designed using Voltage Sourced Converter (VSC) technology which will provide further security of supply benefits in the form of frequency/voltage control and stability to the three areas in which it will connect. As part of the early stage development of the project, key participants and stakeholders will be established. NOTE BY ENTSO-E: The project's grid connection request to the Swedish transmission network has been denied by the Swedish TSO Svenska kraftnät in February 2022. |  |  | Lithuania - Sweden - 600 | Lithuania - Sweden - 600 - Latvia - - <1000 | Latvia - Sweden | 500 | 500
1074 | Pannonian Corridor | The new 400 kV line connecting Serbian and Hungarian transmission systems, initially considered to connect SS Subotica 3 (RS) and SS Sándorfalva (HU). This is, however, not definitely decided, as the bilaterally developed Pre-Feasibility Study is expected to be done soon. This Study will provide much clearer insight into the situation in the area of interest and suggest the optimal substations that should be connected by the new line. Also, this project includes strengthening the North-to-South transmission corridor in Serbian system, by building two new 400 kV lines: SS Sombor 3 – SS Srbobran and SS Srbobran – SS Sremska Mitrovica 2. This is also deemed necessary, as numerous calculations have indicated that the new tie-line may not affect the NTC value enough if it is not accompanied by the two mentioned internal lines. The project can, alongside covering the needs seen in IoSN report, also be seen as a response to the ever-higher requests for integration of renewable sources in the Bačka region, while simultaneously strongly enhancing the security of supply and reliability of the transmission systems' operation in the included countries | EMS, MAVIR | HU ;RS |  | 2033 | 1 | True | False | New | False |  | Each of these investments represents a segment of the new corridor for energy transmission, spanning across Serbian-Hungarian border, simultaneously increasing the NTC on it (which is a need stated in IoSN report) and facilitating the renewable sources integration in the Bačka region (area in the close proximity of the mentioned border). | TYNDP 2020 ;TYNDP 2022 | False | True | http://ems.rs/media/uploads/Plan_razvoja_prenosnog_sistema_2.pdf | Infrastructure to reduce price differentials between EU and/or non-EU countries Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | As the foreseen scope of the project envisages the new interconnection between Serbia and Hungary, it can be seen as another step towards the fully integrated energy market of the CSE region, leading to the noteworthy reduction of the price differentials between the EU and non-EU countries. The additional NTC, vouched for by the commissioning of this project, is expected to be a major asset in the field of system flexibility and stability, especially if the massive capacities of variable RES, predicted along the routes of its investments, are taken into consideration. As the fully integrated market represents one of the main goals set before the system development plans, the new interconnection enveloped by this project will certainly lead the systems of interest in the desired direction, characterized, among other facets, by the balancing flexibility that ensures the reliable energy supply. Since the Bačka region, in the vicinity of the border between Serbia and Hungary, becomes more and more attractive for the investors in the renewable capacities each day, this project represents a guarantee that the energy evacuation from the newly built sources will happen reliably and safely. | Hungary - Serbia - 500 | Hungary - Serbia - 1000 - Hungary - - 1000 - 50001659 | Hungary-Serbia | 500 | 500
1082 | Sea-Socket | The Project aims to set the model for future connection of up to 30GW of Offshore Renewable Energy (ORE) off the west coast of Ireland by connection of up to 700MW per Sea-Socket. Each Sea-Socket includes a high voltage substation platform centrally linking up to four offshore floating wind parks and other OREs. The collected energy will be transmitted via 220kV subsea AC cables to onshore substation(s) located along the Shannon Estuary to be carried onwards by interconnection to Europe. Sea Socket, in its ability to service multiple OREs advances sustainable development by reducing the number of required landfall sites for OREs and removes the investigative, design, consent and construction burden of onward transmission for OREs who can focus on at-sea design and technologies safe in the knowledge of Sea Socket availability. Sea-Socket can make a substantial contribution to facilitating RES integration, and potentially supporting the realisation of emerging opportunities in the production of hydrogen using OREs. The first Sea-Socket will utilise existing grid and interconnectors to Europe. The future roadmap is a vision of multiple Sea-Socket platforms interconnected to Europe. | Siga Hydro Limited | IE |  | 2036 | 1 | False | True | New | False |  |  | TYNDP 2020 ;TYNDP 2022 | False | False |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) Infrastructure to connect energy intensive industry to electricity network (e.g. data hubs,…) | The Project provides the enabling infrastructure to deliver in phase 1, 700MW of offshore wind capacity in Ireland for export to other EU countries utilising existing and new interconnection. It will support the price differentials and trading capabilities between EU member states. Delivers high volumes of RES by the deployment of innovative offshore infrastructure. It will enable the cost-efficient connection of multiple OREs, reduce project development constraints to realise Ireland’s wind resources for use and export. The Project can offer in phase 1, 700MW (plus 1,400MW in subsequent phases) of renewable energy supply to sustainably support the production of hydrogen production contributing to the decarbonisation of the electricity, transport and heating sectors. Sea Socket can supply and connect offshore wind generation to Data Centre clusters throughout Ireland and make a contribution to meeting Data Centre energy needs into the future. |  |  | Internal (Ireland) | 700 | 700
1085 | Malta-Italy Cable Link No.2 | The project consists of a new ~118km long 200MWe HVAC electrical cable interconnection through a submarine cable operating at 220kV between Malta (Maghtab) and Sicily (Ragusa) to be laid in parallel but at a safe distance to the existing ac cable link. The project is part of Maltese Government’s future energy strategy in meeting the 2030 climate and energy targets and the longer term decarbonisation objectives and shall feature in the next update of the Maltese National Energy and Climate Plan. It aims at diversifying the island's energy sources and meet the projected increase in electricity demand from economic growth and electrification of the transport sector. The Project will also strengthen the electricity interconnectivity with the EU electricity network, allow for increased importation of electricity sourced from renewables, optimise the use of local power generation, whilst allowing the increase in local renewable energy sources through the enhancement of the grid stability and balancing of intermittent RES. | Interconnect Malta Ltd | IT ;MT | The Project has been included in the public consultation draft document of the 'Low Carbon Development Strategy' for Malta that was published for public consultation in July 2021 (url: https://meae.gov.mt/en/Public_Consultations/MECP/PublishingImages/Pages/Consultations/MaltasLowCarbonDevelopmentStrategy/Malta%20Low%20Carbon%20Development%20Strategy.pdf )) | 2025 | 1 | True | False | New | False |  |  | TYNDP 2022 | False | False | The Project Description Statement for the scope of the Maltese permitting screening procedure can be accessed in link: https://era.org.mt/era-project/ea_00018_21/ The Project website ( link : www.icm.mt ) is currently under construction. |  |  |  | Malta - - 321 | Malta - Italy | 200 | 200
1086 | Estonia internal grid reinforcement to increase RES connection capability (RRF project) | The project includes several reinforcements mainly in the western part of Estonia. The biggest and most important investments are new Lihula 330 KV substation and Kiisa-Paide 330 kV and Paide-Mustvee 330 kV OHL reconstructions. Together with 330 kV reconstruction also the internal 110 kV network is reinforced where it is foreseen the new RES capacities to be connected. The total effect on connection capability increase of the reconstructions in the western part of Estonia is approximately +200 MW in 110 kV network and +500 MW in 330 kV network. The thermal transmission capacity of the new 330 kV OHL is 1400 MW. Together with the offhsore grid porject reinforcements it will prepare the Estonian power system to be ready to integrate large scale wind parks and additional local RES generation. Together with Offshore project ELWIND the reinforcements allow to increase transmission capacity between Estonia (EE) and Latvia (LV). And in case of EstLink3 these investments also improve to eliminate the internal bottlenects for future possible capacity increase between EE and FI | Elering | EE | it will be a part of the 2021 national development plan that will be issued in december 2021 | 2026 | 2 | False | True | MostlyUpgrade | False |  | The investments are interdependent and the effect of the RES capability increase will be achieved when all investments are completed. | TYNDP 2022 | False | False | https://rrf.ee/wp-content/uploads/2021/05/RRP-Taastekava-eelnou_200521.pdf page 199-205 | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) | Strenghtening the west part of Estonia allows to connect potential off-shore grid connection elements as the majority of the planned landing points for off-shore grid and possible off-shore wind parks are located in this area. Project improves significantly transfer capacities, security of supply and possibilities to connect new generation (mainly RES) in the western part of Estonia where high voltage 330 kV network was insufficient in the past. In the western part of Estonia large amount of new generation and new grid elements are planned and therefore additional reactive power compensation is needed. The project will add significant amount of additional reactive power reserves. |  |  | Estonia internal | 700 | 700
1088 | Latvia and Estonia Hybrid Off-Shore interconnector | The ELWIND project is joint Latvia and Estonia off-shore wind park together with a hybrid interconnector project in the Baltic Sea with planned installed production capacity up to 1000 MW and must be constructed until 2030. The project has been initiated by the Memorandum of Understanding signed in 2020 by Ministry of Economics in Latvia and Ministry of Economics and Communication in Estonia. The project is planned as hybrid interconnector between Latvia and Estonia with off-shore substation in between for the off-shore wind park connection. The project is under development and the exact location and amount of offshore substations will be determined by ongoing studies. | AS Augstsprieguma tikls (AST) and AS ELERING | EE ;LV | NA | 2030 | 1 | True | False | New | False |  | In the ELWIND project currently there are two main investments (ID 1755 and ID 1761) for the off-shore wind connection to the transmission network in Latvia and Estonia. The rest of investments are important to transfer off-shore wind energy, up to 1000 MW, to main consumption centers in Baltic Sea region. | TYNDP 2022 | False | False | https://www.ast.lv/en/events/ast-and-elering-will-jointly-seek-best-solution-grid-connection-offshore-wind-park-baltic https://elering.ee/en/elering-seeking-solutions-order-connect-estonian-latvian-international-offshore-wind-farm-power | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Project improves significantly transfer capacities, security of supply and possibilities to connect off-shore wind parks (max 1000 MW) from Estonian and Latvian wind areas. Crossborder flows between Estonia-Latvia will increase after completion of EstLink 3 due to transit flows from Finland towards Latvia. After completion of EstLink3, the bottleneck between Estonia and Finland will move to Estonia-Latvia border. Considering the increase of RES energy and off-shore wind, it is necessary to add fourth Estonia-Latvia interconnection. High capacity offshore wind connection to the Baltic States onshore grid. The infrastructure developments are very crucial to reduce RES curtailment and provide energy transfer to main consumption areas in Estonia and Latvia |  | Estonia - Latvia - 700 - Estonia - - <1000 Latvia - - <1000 | Estonia - Latvia | 1000 | 1000
1092 | Triton Link: offshore hybrid HVDC interconnector Belgium – Denmark | The construction of a dual-purpose offshore hybrid HVDC interconnector between Belgium and Denmark integrating 3 GW of offshore wind in the Danish Exclusive Economic Zone in the North Sea. This project creates a first transmission link between the Danish and Belgian electricity transmission systems. It is an offshore hybrid project due to merging two purposes: i) interconnecting two countries and ii) connecting offshore RES. The Danish government has approved the construction of an artificial island in the Danish part of the North Sea. The connection of offshore wind will be done in two steps: 3GW towards 2030 or as soon as possible after and 10GW after 2030. The exact integration of the hybrid HVDC interconnector to offshore & onshore grid connection nodes in Belgium & Denmark remains to be further studied. | Energinet and Elia Transmission Belgium | BE ;DK | Planned to be included in the next National Development Plans of Denmark and Belgium (2022) | 2031 | 1 | True | False | New | False |  | The offshore hybrid interconnector between Belgium and Denmark integrating the offshore wind on the new Danish Energy Island is split into two investments as the transport capacities of the connections to Belgium and Denmark are different. Both interconnections are needed to integrate the planned 3GW of offshore wind of the Danish Energy Island to the onshore systems. | TYNDP 2022 | False | False |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project increases the degree of interconnectivity between the Belgian and Danish bidding zones and possibility of higher market exchanges which leads to higher price convergence. This is also a key trigger of the ITEG targets. This project has an adequacy contribution due to decreasing figures of installed conventionals and increasing RES. The project also creates a direct link between two countries which aren't interlinked yet. This is also a key trigger of the ITEG targets. Dual purpose hybrid interconnection enables both direct RES (3GW offshore wind) and indirect RES (avoided curtailment) integration through increased XB transmission capacity between bidding zones. This project satisfies this need in a cost-efficient manner. |  | Belgium - - <1000 Denmark - - <1000 | Belgium - OBZ Energy Island (DK) OBZ Energy Island (DK) - Denmark | 2000 1400 | 2000 1400 | Adequacy benefits are deemed too low for the creation of an interconnection between two not yet directly interconnected countries.
1094 | Estlink 3 | 3rd HVDC connection between Finland and Estonia. On FI side also includes 400 kV transmission network upgrade and extension to the landing point to connect Estlink 3 converter station to the rest of the transmissions system. The landing point is expected to be Inkoo substation, but is not yet decided. On EE side the project also includes 330 kV transmission network upgrade and extension to the landing point to connect Estlink 3 converter station to the rest of the transmissions system. The exact landing point on EE territory is in planning status and not specified yet. | Fingrid and Elering | EE ;FI | Not yet included in the national development plan | 2040 | 1 | True | False | New | False |  | On the Finland side, getting full capacity of Estlink 3 will likely require at least Inkoo-Hikiä 400 kV reinforcement. | TYNDP 2022 | False | False | The concept is investigated for example in Fingrid's network vision: https://www.fingrid.fi/globalassets/dokumentit/fi/kantaverkko/kantaverkon-kehittaminen/fingrid_network_vision.pdf | Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to reduce price differentials between EU and/or non-EU countries Capability for Black Start & Islanding Operation Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | After Baltics syncronization with Continental Europe synchronous area the major challenge is to ensure system stability and to be ready for islanding in case of extreme contingencies. The capability to ensure frequency stability in case of major faults is based on HVDC links that provide fast frequency control. Last year and future perspectives are showing very high price differences between Estonia and Finland market areas. Additional market capacity between these areas are necessary to be implemented. New HVDC link will provide additional black start capabilities in both Finland and Estonia power system. The need for black start capability will be increased in the future due to higher risk of islanding of Baltics and replace conventional generation with RES. With significant increase of RES in Estonia and Finland especially with off- and on-shore wind parks additional transfer capacities are required. It allows to increase export and import for maximum utilization of cost efficient RES generation in both sides of the system. |  | Estonia - Finland - 700 - Estonia - - <1000 | Finland - Estonia | 700 | 700
1095 | Aurora line 2 (4th AC Finland-Sweden north) | Fourth AC 400 kV overhead line between Finland north and Sweden SE1. Strengthening the AC connection between Finland and Sweden is necessary due to market needs, security of supply in the Nordics, new RES generation and substantial investmentents in clean hydrogen economy. | Fingrid, Svenska Kraftnät | FI ;SE | Not included yet | 2035 | 1 | True | False | New | False |  |  | TYNDP 2022 | False | False | The concept is investigated for example in Fingrid's network vision: https://www.fingrid.fi/globalassets/dokumentit/fi/kantaverkko/kantaverkon-kehittaminen/fingrid_network_vision.pdf | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to tackle a Need identified by one of the European ITEG indicators referring to the 15% interconnection target for 2030: 1. Reduce the price differential between EU countries to below 2EUR/MWh. 2. Contribute to pushing ratio between nominal transmission capacity and installed RES capacity past 30%. 3. Contribute to pushing ratio between nominal transmission capacity and peak load past 30%. Infrastructure to connect energy intensive industry to electricity network (e.g. data hubs,…) | Adds market capacity 800 MW. Improves local power balance and mitigates risk of power failures in Sweden and Finland. Adds market capacity 800 MW. Contributes to all three interconnection targets. Supports the connection of energy intensive industry especially in Northern Sweden. | Finland - Sweden - 1700 | Finland - Sweden - 2500 - | Finland - Sweden | 800 | 800
1096 | Beznau - Mettlen | This project • increases the capacity between Switzerland and its northern neighbours. This enables to connect large renewable generation in Northern Europe to pump storage devices in the Alps, thus noticeably increasing the mutual balancing between both regions. • comprises the optimization of the existing route by voltage conversion to 380 kV and a partial reinforcement. • is not new, it is part of the TYNDP 2020 Project Swiss Roof I. | Swissgrid | CH | Bericht zum Strategischen Netz 2025, Switzerland, 2015, page 184, https://www.swissgrid.ch/dam/swissgrid/projects/strategic-grid/sg2025-technical-report-de.pdf | 2028 | 3 | False | True | MostlyNew | False |  | no clustering | TYNDP 2022 | False | True | https://www.swissgrid.ch/content/swissgrid/en/home/projects/project-overview/beznau-birr.html https://www.swissgrid.ch/content/swissgrid/en/home/projects/project-overview/niederwil-obfelden.html | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | This project contributes to lowering the price differentials between Switzerland, Germany and Austria. This project contributes to the adequacy in view of the nuclear phase-out and the development of renewables and pump hydro storage devices. This project is located in a highly meshed part of the transmission grid and therefore helps accommodate such flows. | Germany - Switzerland - 1550 | Germany - Switzerland - 1550 - Germany - - 5000 - 10000 Switzerland - - <1000 | Germany - Switzerland | 700 | 0
1097 | Upgrade to Konti-Skan | This project will increase the capacity on the existing HVDC connections Konti-Skan 1 and 2 connecting SE3 and DK1 by 700 MW, resulting in a total of 1400 MW capacity between SE3 and DK1. Please note that the total capacity is still under investigation. but it will be a maximum increase of 700 MW. Konti-Skan 1 and 2 will achieve their technical lifespans in the mid-2030s and are planned to be replaced. The entire facilities including stations, control systems, cables and overhead lines for each connection are in need of replacement. The "Upgrade to Konti-Skan" project does not include the replacement capacity nor the cost of the replacement of the existing Konti-Skan 1 and 2. | Svenska kraftnät, Energinet | DK ;SE | 10-Year Grid Investment Plan 2020-2029, Sweden, 2019, p.26: Available online: {https://www.svk.se/siteassets/om-oss/rapporter/2020/10-year-development-plan-2020-2029.pdf} | 2032 | 1 | True | False | MostlyNew | False |  |  | TYNDP 2022 | False | False |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) | Project connects two market areas (DKW and SE) with high price differentials between EU countries. Adding more power transfer capabilities and facilitate more power flexibilities between two countries. The project will enable the integration of RES. More interconnection capacity will improve capability of balancing the system. The project increases system size, thus facilitates sharing of ancillary service. | Denmark (West) - Sweden - 1200 | Denmark (West) - Sweden - 1700 - Denmark - - <1000 | Sweden - Denmark | 700 | 700
1098 | Offshore Wind LT 2 | Second stage for integration of additional 700 MW off-shore wind farms in Baltic Sea near Lithuania coast. Onshore connection to 330 kV Darbenai substation. Studies are in progress concerning environmental assessment and maritime planning. | LITGRID AB | LT | "Development plan of the electric power system and transmission grid. 2021-2030" (https://www.litgrid.eu/uploads/files/dir580/dir29/dir1/10_0.php), June 2021, pages 23, 26. | 2030 | 1 | False | True | New | False |  | Taking into account that till 2030 Darbenai substation will be connection point for 700 MW HVDC Harmony link and 700 MW offshore wind park (another planned project 1042 Offshore LT1), connection of additional 700 MW offshore wind farm to Darbenai substation will require to strengthen 330 kV network in Lithuania - build new 330 kV lines. | TYNDP 2022 | False | False |  | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) Infrastructure to connect energy intensive industry to electricity network (e.g. data hubs,…) Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | Generation from offshore wind will increase system adequacy for Lithuania. New offshore wind farms will provide sufficient electricity meeting demand increase (electrification of transport sector, P2H, electrolysers). New offshore wind farms will ensure decarbonization of energy intensive industry (green hydrogen for industry). Offshore wind farm will increase power flows in 330 kV network, especially in n-1 situations. To remove internal congestions, it is planned to build two 330 kV internal AC lines. |  |  | Internal (Lithuania) | 700 | 700
1100 | Reinforcement of the existing CZ-DE interconnector (Hradec - Röhrsdorf) on the CZ side | The project consists in the modernization of an existing double-circuit 400 kV line between the Hradec and Röhrsdorf substations on the Czech side. The project will be implemented only in the section located in the Czech Republic, on an existing route so as to minimize environmental impacts and appropriation of additional land. The project contributes to maintaining reliable supply for domestic demand in case of power shortage in the Czech Republic, using imports from surplus generation in the north of Germany. | CEPS | CZ ;DE | Ten-year investment plan for the development of the TS 2021 – 2030, CZ, 2021, V445/446 – Upgrade, 103 pg., https://www.ceps.cz/en/transmission-system-development | 2028 | 3 | True | False | Upgrade | False |  |  | TYNDP 2022 | False | False | Information about Czech development plan can be found on the following link below on the CEPS website: https://www.ceps.cz/en/transmission-system-development | Infrastructure to reduce price differentials between EU and/or non-EU countries Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | This project helps to decrease the curtailed energy in Germany due to extra market transfers (increase of NTC) on the profile DE - CZ which lead to reduction of marginal price. The project contains the upgrade of existing 220 kV lines to 400 kV lines which will reduce infrastructure vulnerability and therefore ensure reliable and secure operation of the grid. This project besides the increase of NTC also consists of reinforcement of internal lines and therefore facilitates the future need for cross-border flows. The project is aiming at facilitation of the power flows from the RES generation in the northern part of Europe and western part of CZ therefore promotes RES integration. | Czech Republic - Germany - 1000 | Czech Republic - Germany - 1000 - Germany - - 5000 - 10000 | Czech Republic - Germany | 0 | 500
1102 | Mettlen - Ulrichen | This project • increases the capacity between Switzerland and its northern neighbours. This enables to connect large renewable generation in Northern Europe to pump storage devices in the Alps, thus noticeably increasing the mutual balancing between both regions. • comprises the reinforcement of the existing 220 kV line to 380 kV • is not new, it is part of the TYNDP 2020 Project Swiss Roof I. | Swissgrid | CH | https://www.swissgrid.ch/dam/swissgrid/projects/strategic-grid/sg2025-technical-report-de.pdf | 2035 | 3 | False | True | MostlyNew | False |  | no clustering | TYNDP 2022 | False | True | https://www.swissgrid.ch/content/swissgrid/en/home/projects/project-overview/mettlen-ulrichen.html | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Reduction of the loop flows occurrence in the borders between CZ-DE, DE-PL, DE-NL-BE-LU-FR-DE | This project contributes to lowering the price differentials between Switzerland, Germany and Austria. This project contributes to the adequacy in view of the nuclear phase-out and the development of renewables and pump hydro storage devices. This project is located in a highly meshed part of the transmission grid and therefore helps accommodate such flows. | Germany - Switzerland - 1550 | Germany - Switzerland - 1550 - Germany - - 5000 - 10000 Switzerland - - <1000 | Germany - Switzerland | 0 | 200
1103 | Bickigen - Chippis | This project • increases the capacity between Switzerland and its northern neighbours. This enables to connect large renewable generation in Northern Europe to pump storage devices in the Alps, thus noticeably increasing the mutual balancing between both regions. • comprises the optimization of the existing route by voltage conversion to 380 kV • is not new, it is part of the TYNDP 2020 Project Swiss Ellipse I. | Swissgrid | CH | Bericht zum Strategischen Netz 2025, Switzerland, 2015, page 184, https://www.swissgrid.ch/dam/swissgrid/projects/strategic-grid/sg2025-technical-report-de.pdf | 2028 | 3 | False | True | MostlyUpgrade | False |  | no clustering | TYNDP 2022 | False | True | https://www.swissgrid.ch/content/swissgrid/en/home/projects/project-overview/bickigen-chippis.html | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. | This project contributes to lowering the price differentials between Switzerland, Germany and Austria. This project contributes to the adequacy in view of the nuclear phase-out and the development of renewables and pump hydro storage devices. This project is located in a highly meshed part of the transmission grid and therefore helps accommodate such flows. | Germany - Switzerland - 1550 | Germany - Switzerland - 1550 - Germany - - 5000 - 10000 Switzerland - - <1000 | Germany - Switzerland | 500 | 0
1104 | Niederstedem - Roost | It is planned to upgrade the capacity of the existing 220 kV overhead line between the substations Roost-Flebour-Bauler and the substations Bauler-Niederstedem. For this reinforcement the options are either the implementation of High Temperature Low Sag (HTLS) conductors or a reconstruction of the tie-line in the existing route. | Amprion, Creos | DE ;LU | NDP1; Germany, Netzentwicklungsplan 2035 Version 2021, Project 505, p. 680; NDP LUX 2040 Version 2021 p.26 | 2030 | 2 | True | False | Upgrade | False |  | high priority on upgrading existing transmission OHL between Flebour and Bauler for Creos. | TYNDP 2022 | False | True | Further information of the project, its investments and their necessity particularly for the German Energiewende can be found in the German grid development plan (mostly in German): http://www.netzentwicklungsplan.de/en/front | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. |  | Germany - Luxemburg - 400 | Germany - Luxemburg - 400 - Germany - - 5000 - 10000 Luxemburg - - <1000 | Germany - Luxemburg | 400 | 400
1105 | Georgia-Romania Black Sea (submarine) interconnection cable project | Georgia-Romania Black Sea submarine interconnection project will connect Georgian power system (and South Caucasus region) to Synchronous grid of Continental Europe. Mentioned project will assist energy security of European Union and Caucasus region, support development of renewable energy sector, increase transit opportunities and trade options between European Union and South Caucasus region which will have positive impact on electricity producers and transmission system operators. Based on preliminary data, construction of double-circuit 500 kV between existing 500 kV SS Jvari and new 500 kV SS Anaklia will be constructed. The next part will be two-pole 500 kV DC submarine cable Anaklia-Constanta. In order to implement such connection, construction of 500/500 kV DC converter station with installed capacity of 2x500 MW at Anaklia substation is considered. Implementation of this project may require additional reinforcement of high voltage network of mentioned interconnected power systems. Feasibility study of the Georgia-Romania Black Sea submarine transmission and digital line construction project has commenced on May 11, 2022 and will continue for 18 months period. | JSC Georgian State Electrosystem (GSE) | GE ;RO | Ten-Year Network Development Plan of Georgia 2021-2031, Georgia, 2021, p 66, https://www.gse.com.ge/sw/static/file/TYNDP_GE-2021-2031_ENG_NEW.pdf | 2029 | 1 | True | False | New | False |  | Since the project is under consideration, the parameters of its constituent components have not been currently clarified. | TYNDP 2022 | False | False |  | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) Improve system flexibility and stability e.g. improve system or local ramp rate, improve transient stability or RoCoF to meet system Needs. | This project will facilitate cross-border trading between EU and Caucasus regions. Enable both of them to accomodate more RES in the system and trade with this clean energy and increase trading competition. Due to high capacity of the link, it enables both Romanian and Georgian systems to integrate more renewable resources, reducing curtailment because of higher transfer capacity through the link. Especially, during night regimes when there is a risk of having generation surplass. The link will be equiped with VSC type converters, wich have the capability to control active and reactive power independently, meaning it can improve voltage controllability and quality as well. The project will increase both system flexibility, as the type of converter is VSC meaning continuous control of active and reactive power. VSC gives fast control capability of frequency, voltage and power reversal in case of need. Due to these features the project will enhance flexibility and stability. |  |  | Georgia - Romania | 1000 | 1000
1106 | Bornholm Energy Island (BEI) | Both Parties aim to establish an innovative new hybrid offshore interconnection between the Danish Zealand, the Danish Island of Bornholm, and Germany by 2030. This hybrid interconnector, referred to as the “Bornholm Energy Island Project” (BEI) is not only intended as an interconnection between both countries, but also to integrate 2 GW of offshore windfarm capacity, located southwest of Bornholm, in the Exclusive Economic Zone of Denmark. The Parties have the ambition to realise this via a multi-terminal, multi-vendor DC solution (MTDC) on the island of Bornholm, which would be a technical novelty for the European transmission grid. Moreover, the Parties want to establish a true energy hub, with the possibility for future extensions including the connections of further interconnectors to other countries or possibly the integration of additional generation or load, including but not limited to Power-to-X facilities. With this project, the Parties aim to support the EU Commission’s new Green Deal and climate targets, help to reduce the overall CO2 emissions of the European energy system and strengthen the integration of the internal European electricity market as well as security of supply. | Energinet, 50Hertz | DE ;DK | The BEI project is not yet included in the last National Development Plans of Denmark or Germany and therefore the additional internal required grid reinforcements are not yet analysed. In the Danish case, the upcoming Danish 'Strategic Investment Plan' will include the BEI project. The BEI project is presently analyzed in various feasibility studies at wider regional level. | 2030 | 1 | True | False | New | False |  | The BEI investment items need to be clustered and thereby realised together to meet its full benefit. The investment items are mutually dependent on each other. Realising one investment contributes to the realisation of the full potential of another investment item. Without the wind farm connections, the configuration would merely provide interconnection while the RES integration would still require additional (radial) connections to shore. And without the interconnection links, the concept would be a single hub to shore, while missing the opportunities of European-wide market integration and sharing of reserves. Presently, all investments in the BEI project are ‘under consideration’, with a provisional commissioning for 2030. | TYNDP 2022 | False | False | The cooperation by the Project Partners build on a Letter of Intent signed in January, 2021, following a Letter of Intent signed by the Danish and German ministries in December, 2020 (https://www.bmwi.de/Redaktion/DE/Downloads/J-L/letter-of-intent-between-german-minister-denmark-minister-hybrid-offshore.html). https://www.50hertz.com/en/News/FullarticleNewsof50Hertz/id/7388/50hertz-and-energinet-sign-letter-of-intent-for-offshore-hub-bornholm-energy-island-in-the-baltic-sea https://ens.dk/en/our-responsibilities/wind-power/energy-islands/denmarks-energy-islands https://en.energinet.dk/Green-Transition/Energy-Islands | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure designed to offer more supply options to isolated areas | This project will both integrate offshore wind and provide new interconnection capacity, reducing price differentials between EU countries. This project will enable the integration of RES. More interconnection capacity will improve capability of balancing the system. This project enables direct cost-efficient connection of at least 2000 MW offshore wind generation capacity to two market areas. This project could enable additional supply options for the local Bornholm island grid, which to date is only connected to SE04 via a 66 kV AC connection. |  | Germany - - 5000 - 10000 Denmark - - <1000 | Germany-Bornholm Energy Island Denmark (DKE)-Bornholm Energy Island | 2000 1200 | 2000 1200
1107 | EuroAfrica Interconnector | The EuroAfrica Interconnector comprises the electricity interconnection between the grids of Egypt, Cyprus and Greece (Europe) through a subsea DC cable and with HVDC onshore converter stations at each connection point, with a total capacity of 2000MW. The project is an energy highway bridging Africa and Europe, with a total length of 1396 km (Egypt-Cyprus 498km) . It creates a reliable alternative route for the transfer of electric energy to and from Europe. | EuroAfrica Interconnector Ltd | CY ;EG | Title of the document: “ΔΕΚΑΕΤΕΣ ΠΡΟΓΡΑΜΜΑ ΑΝΑΠΤΥΞΗΣ ΣΥΣΤΗΜΑΤΟΣ ΜΕΤΑΦΟΡΑΣ 2021-2030” Country: Cyprus Year: 2021 Page number: 9 TSO: TSOC url: https://tsoc.org.cy/files/electrical-system/tydplan/%CE%94%CE%A0%CE%91%CE%A3%CE%9C%202021-2030%20web.pdf | 2026 | 3 | True | False | New | False |  |  | TYNDP 2022 | False | False |  |  |  |  | Cyprus - - <1000 | Cyprus - Egypt | 1000 | 1000
1109 | Basilicata - Campania reinforcements | New 400 kV lines between Basilicata and Campania and in the northern area of Benevento will increase the southern/northern artery, will reduce congestions by increasing NTC between market zones and will integrate new RES power attended in the South of Italy. | Terna SpA | IT | Piano di Sviluppo 2021 – Avanzamento Piani di Sviluppo Precedenti – Avanzamento Centro Sud (546-P) Piano di Sviluppo 2021 (553-N) https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete/pag186-323 | 2030 | 2 | False | True | New | False |  | New 400 kV lines between Basilicata and Campania and in the northern area of Benevento will increase the southern/northern artery, will reduce congestions by increasing NTC between market zones and will integrate new RES power attended in the South of Italy. General comment for all projects: the scope of TYNDP project analysis is broader than national. This was done in line with TYNDP 2020 and the possibility of de-clustering projects will be considered in the future. | TYNDP 2022 | False | False |  | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Increase RES integration |  |  | Italian Northern border Italy internal (ITs-ITcs) | 500 500 | 500 500
1110 | Sicily - Calabria | New 400 kV subsea cable between Sicilia and Calabria will increase NTC between market zones and will integrate new RES power attended in Sicily and reduce dispatching cost for the system. | Terna SpA | IT | Piano di Sviluppo 2021 https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete/page 320 | 2026 | 2 | False | True | New | False |  |  | TYNDP 2022 | False | False |  | Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to reduce price differentials between EU and/or non-EU countries | Increase RES integration Increase market exchanges between italian market zones |  |  | Italian northern border Italy internal (ITs-ITca) | 500 500 | 500 500
1112 | GRITA 2 | The project concerns the strengthening of the GR-IT border by the development of a new HVDC link that will operate along with the existing HVDC link between the two countries. The project consists mainly in the development of new HVDC submarine interconnection between Italian and Greek transmission systems. A preliminary solution foresees a 2nd interconnection between Galatina and Arachthos, and the development of new converter stations in parallel with the current link. The presence of two interconnections will lead to increase transfer capabilities and guarantee higher reliability in terms of power exchanges between Italy and Greece. The concerned TSOs, IPTO and Terna, signed an agreement for studying the development of a new HVDC link (studies completion within 2021) to provide the best technical solution that will guarantee an increase of the current NTC on Italy-Greece border of at least 500 MW (up to 1000 MW NTC increase, including internal reinforcements) in order to address future challenges and EU targets set. Terna included the new link in its NDP2021 as project planned to be realized within 2030, while evaluations by IPTO are progressing for the inclusion of the project (currently under consideration) in its NDP | TERNA;IPTO | GR ;IT | Italian NDP 2021- Piano di Sviluppo / page 316/ https://www.terna.it/it/sistema-elettrico/rete/piano-sviluppo-rete | 2031 | 1 | True | False | New | False |  |  | TYNDP 2022 | False | False |  | Infrastructure to reduce price differentials between EU and/or non-EU countries Infrastructure and/or market design to provide balancing flexibility (e.g. international pooling / sharing of reserves, coordinated development of reserve capacity) Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The project contributes in reducing price differentials indicated between Italy and Greece in the future due to the generation shift, enabling lower and more balanced wholesale prices. The project, as a new interconnector between Italy and Greece, will provide balancing flexibility to the Greek and Italian power systems. The project will allow the exploitation of RES potential located in west Greece and south Italy and will reduce future RES curtailments in Italy and Greece. | Greece - Italy - 1500 | Greece - Italy - 500 - Italy - - 1000 - 5000 | Greece - Italy | 500 | 500
1119 | Bisamberg (AT) - Wien SO (AT) - Parndorf (AT) | Increase of Renewables is political and societal goal. This project is needed to connect wind and PV generation in the relevant areas to the transmission system and brings also an increase of the security of supply as the capacities increase and additional connections to the distribution systems are created. | Austrian Power Grid | AT | APG NDP21; Austria; 2021; Chapter 5.1; Page 98; https://www.apg.at/de/Stromnetz/Netzentwicklung | 2031 | 1 | False | True | Upgrade | False |  |  | TYNDP 2022 | False | True | https://www.apg.at/de/Stromnetz/Netzentwicklung | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) Infrastructure to connect energy intensive industry to electricity network (e.g. data hubs,…) | Projects improves connection of wind an PV generation with sufficient capacity to the transmission system and enables future RES development. Projects improves connection of wind an PV generation with sufficient capacity to the transmission system and enables future RES development. The project provides the opportunity to integrate additional electrolysers in the region. Through the project, there is an opportunity to decarbonize and integrate additional energy intensive industry in the region. |  |  | Austria internal | 3000 | 3000
1120 | Wien SO (AT) – Ternitz (AT) – Hessenberg (AT) | Increase of Renewables is political and societal goal. This project is needed to connect wind and PV generation in the relevant areas to the transmission system and brings also an increase of the security of supply as the capacities increase and additional connections to the distribution systems are created. | Austrian Power Grid | AT | APG NDP21; Austria; 2021; Chapter 5.1; Page 98; https://www.apg.at/de/Stromnetz/Netzentwicklung | 2033 | 1 | False | True | Upgrade | False |  |  | TYNDP 2022 | False | True | https://www.apg.at/de/Stromnetz/Netzentwicklung | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) Infrastructure to connect energy intensive industry to electricity network (e.g. data hubs,…) | Projects improves connection of wind and PV generation with sufficient capacity to the transmission system and enables future RES development. Projects improves connection of wind and PV generation with sufficient capacity to the transmission system and enables future RES development. The project provides the opportunity to integrate additional electrolysers in the region. Through the project, there is an opportunity to decarbonize and integrate additional energy intensive industry in the region |  |  | Austria | 750 | 750
1121 | Hessenberg (AT) - Weißenbach (AT) | Increase of Renewables is political and societal goal. This project is needed to connect wind and PV generation in the relevant areas to the transmission system and brings also an increase of the security of supply as the capacities increase. | Austrian Power Grid | AT | APG NDP21; Austrian; 2021; 19-4; Page 75; https://www.apg.at/de/Stromnetz/Netzentwicklung | 2029 | 2 | False | True | Upgrade | False |  |  | TYNDP 2022 | False | True | https://www.apg.at/de/Stromnetz/Netzentwicklung | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructure to decarbonize other energy sectors. (e.g. Electrolysers, P2H, …) Infrastructure to connect energy intensive industry to electricity network (e.g. data hubs,…) | Projects improves connection of wind and PV generation with sufficient capacity to the transmission system and enables future RES development. Projects improves connection of wind and PV generation with sufficient capacity to the transmission system and enables future RES development. The project provides the opportunity to integrate additional electrolysers in the region. Through the project, there is an opportunity to decarbonize and integrate additional energy intensive industry in the region. |  |  | Austria | 600 | 600
1122 | Offshore Wind connection Centre Manche 1 | 320 kV HVDC hub in Normandy, connecting a 1 GW offshore wind project (Centre Manche 1) and 250 MW from a second offshore wind project (Centre Manche 2) to the 400 kV substation of Menuel. | RTE | FR |  | 2031 | 1 | False | True | New | False |  |  | TYNDP 2022 | False | False | https://www.rte-france.com/projets/nos-projets/projet-deolien-en-mer-au-large-de-la-normandie | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Capability for Black Start & Islanding Operation Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) | The offshore Wind Connection Centre Manche 1 is needed to connect future offshore windfarms and therefore contribute to the increase of renewable energy share in the generation mix. The offshore Wind Connection Centre Manche 1 is needed to connect future offshore windfarms and is designed to optimize the evacuation of the produced energy. Depending on the design of the HVDC converter station which is not defined at this stage, the project could contribute to black start/islanding operations. An HVDC system is able to contribute to voltage regulation on the network both during steady state and fault conditions, by producing or consuming reactive power within the specified range. |  |  | France internal | 1250 | 1250
1123 | Offshore Wind Connection Centre Manche 2 | 320 kV HVDC hub in Normandy, connecting a 1,5 GW offshore wind project (Centre Manche 2) to a 400 kV substation in the Normandy region (Calvados or Seine maritime). | RTE | FR |  | 2032 | 1 | False | True | New | False |  |  | TYNDP 2022 | False | False |  | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Capability for Black Start & Islanding Operation Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) | The offshore Wind Connection Centre Manche 2 is needed to connect future offshore windfarms and therefore contribute to the increase of renewable energy share in the generation mix. The offshore Wind Connection Centre Manche 2 is needed to connect future offshore windfarms and is designed to optimize the evacuation of the produced energy. Depending on the design of the HVDC converter station which is not defined at this stage, the project could contribute to black start/islanding operations. Thanks to its AC voltage and reactive power control capability, an HVDC system is able to contribute to voltage regulation on the network both during steady state and fault conditions, by producing or consuming reactive power within the specified range. |  |  | France internal | 1250 | 1250
1124 | Offshore Wind Connection South Britanny | 750 MW Offshore HVAC wind hub connecting two different floating windfarms | RTE | FR |  | 2029 | 1 | False | True | New | False |  |  | TYNDP 2022 | False | False |  | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The offshore Wind Connection South Brittany is needed to connect future offshore windfarms and therefore contribute to the increase of renewable energy share in the generation mix. The offshore Wind Connection South Brittany is needed to connect future offshore windfarms and is designed to optimize the evacuation of the produced energy. |  |  | France internal | 750 | 750
1125 | Offshore Wind Connection Occitanie | 750 MW offshore wind connection hub, connecting two different floating windfarms | RTE | FR |  | 2030 | 1 | False | True | New | False |  |  | TYNDP 2022 | False | False |  | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The offshore Wind Connection Occitanie is needed to connect future offshore windfarms and therefore contribute to the increase of renewable energy share in the generation mix. The offshore Wind Connection Occitanie is needed to connect future offshore windfarms and is designed to optimize the evacuation of the produced energy. |  |  | France internal | 750 | 750
1126 | Offshore Wind Connection PACA | 750 MW offshore wind connection hub, connecting two different floating windfarms | RTE | FR |  | 2030 | 1 | False | True | New | False |  |  | TYNDP 2022 | False | False |  | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | The offshore Wind Connection PACA is needed to connect future offshore windfarms and therefore contribute to the increase of renewable energy share in the generation mix. The offshore Wind Connection PACA is needed to connect future offshore windfarms and is designed to optimize the evacuation of the produced energy. |  |  | France internal | 750 | 750
1127 | Offshore Wind Connection South Atlantic | Offshore wind connection project under study in the South Atlantic region, between 1000 and 2000 MW | RTE | FR |  | 2032 | 1 | False | True | New | False |  | Investment needed to minimise offshore wind spillage | TYNDP 2022 | False | False |  | Infrastructure to address system adequacy deficiencies and/or mitigate the risk of power failures. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment Infrastructrure improves voltage stability by offering reactive power controllability of converters by system operator(s) | The offshore Wind Connection South Atlantic is needed to connect future offshore windfarms and therefore contribute to the increase of renewable energy share in the generation mix. The offshore Wind Connection South Atlantic is needed to connect future offshore windfarms and is designed to optimize the evacuation of the produced energy. Thanks to its AC voltage and reactive power control capability, an HVDC system is able to contribute to voltage regulation on the network both during steady state and fault conditions, by producing or consuming reactive power within the specified range. |  |  | France internal | 1250 | 1250
1129 | New RES at Minho region | This project creates conditions for the connection of additional RES in Minho region, where the RES potential is high, and contributes to the maintenance of NTC values between PT and ES. | Rede Elétrica Nacional | PT | NDP 1, Portugal, Draft NDP 2022-2031 (2021); Main report, Page 13 (https://www.erse.pt/media/nx3ittiy/pdirt-2022-2031-mar%C3%A7o-2021-relat%C3%B3rio-final.pdf); Apendix 11, page 5 (https://www.erse.pt/media/kdgjy4jl/pdirt-2022-2031-mar%C3%A7o-2021-anexos.pdf) | 2029 | 2 | False | True | MostlyNew | True | 2.16.1 |  | TYNDP 2022 | True | True |  | Infrastructure to facilitate and accommodate future scenarios, cross-border flows or loop flows. Infrastructure designed to enable cost-efficient grid connection of high volumes of RES and/or reduce RES curtailment | Internal sutdies showed high level of congestion in the network resulting from the integration of RES (wind and Solar) where the RES potential is considerably high. Project for integration of RES (Wind and Solar). |  |  | Internal (Portugal) | 400 | 400

## Trans.Investments
TYNDP 2022 Transmission projects - General information on transmission investments | [8 empty] | Technical characteristics of the investment | [10 empty] | Costs of the investment |  |  |  | CBA indicators at investment level – B8.0 Stability (Transient, voltage and frequency stability) |  |  | Residual environmental impact |  |  | Residual social impact |  |  | Other residual impact
Investment number | Investment Name | This investment belongs to project number… | Description of the investment | Commissioning Year | Status ID 1 : Under Consideration, 2 : In Planning but not permitting, 3 : In permitting, 4 : Under Construction | Is Main Investment(s) | Progress of the investment since TYNDP2020 | Explanation in case of delay or reclustering | Type of Element | Substation From | Substation To | Technology | Type of HVDC | Total route length (km) | Nominal voltage (kV) | Capacity of the investment (MW) | MVA | Type of converter | Mvar | Estimated CAPEX (MEUR) | Sustaining CAPEX (Meuro) | Estimated OPEX (MEUR) | Cost Uncertainty Range | Transient stability | Voltage stability | Frequency stability | Distance (km) | Type of sensitivity | Additional information | Distance (km) | Type of sensitivity | Additional information | Other residual impact
4 | V.Minho -R.Pena-Feira | 1 | New double-circuit 400kV OHL Vieira do Minho (PT) - Ribeira de Pena (PT) - Feira (PT). | 12-2022 | 4 | TRUE | Investment on time | Although the construction started on the section Feira-Ribeira de Pena, there is a public opposition to the project that is delaying the construction. Section V.Minho-Ribeira de Pena was comissioned in 2021. | ACTransmissionLine | V.Minho (by Ribeira de Pena) | Feira (by Ribeira de Pena) | AC | None | 131 | 400 | 0 | 2083 |  |  | 45.8 | 0 | 0.153 | ±10%% | ++ | ++ | 0 | 13 7 | Other Other | Habitats Directive Birds Directive Habitats Directive IUCN key biodiversity áreas | 10 | Other | Globally Important Agricultural Heritage Systems (GIAHS)
474 | Substation Ribeira de Pena | 1 | New 400/60kV substation in Ribeira de Pena. | 12-2021 | 5 | TRUE | Investment on time |  | OnshoreSubstation | Ribeira de Pena (PT) | - | AC | None | 0 | 400 | 0 |  |  |  | 10.867 | 0 | 0.054 | ±10%%
18 | Beariz (ES) - Fontefria (ES) | 4 | New double circuit 400kV OHL between Beariz (ES) - Fontefria (ES). | 06-2024 | 3 | TRUE | Delayed | Delays in the Environmental Impact Assessment process | ACTransmissionLine | Beariz (ES) | Fontefria (ES) | AC | None | 30 | 400 | 0 |  |  |  | 26.53 | 0 | 0.45 | 10%% | ++ | ++ | 0
496 | Fontefria (ES) - Vila Nova de Famalicão (PT) | 4 | New 400kV OHL Fontefria (ES) - Ponte de Lima (PT) - Vila Nova de Famalicão (PT). | 06-2024 | 3 | TRUE | Delayed | Delays in the Environmental Impact Assessment process. Section Vila Nova de Famalicão-Ponte de Lima was comissioned in 2021. | ACTransmissionLine | Fontefria (ES) | Vila Nova de Famalicão (PT) (By Ponte de Lima) | AC | None | 94.71 | 400 | 0 | 1499 |  |  | 39.559 | 0 | 0.161 | 10%% | ++ | ++ | 0 | 0.5 29 3 | HabitatsDirective None HabitatsDirective |  | 1 | HabitatsDirective
498 | SE Fontefria 400/220kV | 4 | New 400kV substation Fontefria (ES), previously O Covelo. | 06-2024 | 3 | TRUE | Delayed | Delays in the Environmental Impact Assessment process | Transformer | Fontefria (ES) | REE | AC | None | 0 | 400 | 0 |  |  |  | 9.04 | 0 | 0.22 | 10%%
499 | Beariz 400kV (ES) | 4 | New 400kV substation Beariz (ES), previously Boboras | 06-2024 | 3 | TRUE | Delayed | Delays in the Environmental Impact Assessment process | OnshoreSubstation | Beariz (ES) | Beariz (ES) | AC | None | 0 | 400 | 0 |  |  |  | 5.01 | 0 | 0.16 | 10%%
500 | Ponte de Lima (PT) | 4 | New 400/150kV substation Ponte de Lima (PT), previously V. Castelo. | 06-2024 | 3 | TRUE | Delayed | Delays due to correlation with other delayed infrastructure investments. | OnshoreSubstation | Ponte de Lima (PT) | Ponte de Lima (PT) | AC | None | 0 | 400 | 0 |  |  |  | 10 | 0 | 0.054 | 10%%
38 | HVDC Gatica-Cubnezais | 16 | New HVDC interconnection in the western part of the border via DC subsea cable in the Biscay Gulf (cable and converters at the end). | 12-2027 | 3 | TRUE | Investment on time |  | OffshoreDCTransmissionCable | Gatica (ES) | Cubnezais (FR) | DC | None | 394 | 400 | 2000 |  | VCS |  | 1950 | 0 | 10.2 | 0% | ++ | ++ | + (between sync areas) | 11 | Other |  | 0.269 | HabitatsDirective
614 | Reschenpass Interconnector | 26 | Interconnector IT-AT | 06-2023 | 4 | TRUE | Investment on time |  | ACTransmissionLine | Nauders (AT) | Glorenza (IT) | AC | None | 26 | 220 | 0 | 450 |  |  | 170 | 0 | 0.43 | 10% | ++ | ++ | 0 | 0 | None |  | 2 | Other | -
1503 | Second HVDC Module IT-ME | 28 | Second HVDC Module (600 MW) of interconnection line between Italy and Montenegro via 445 km 500kV DC subsea cable and converter stations at both ending points. | 12-2026 | 4 | TRUE | Investment on time | Commissioning under review. An update will be given in next TYNDP. | DCTransmissionLine | Villanova (IT) | Lastva (ME) | DC | Bipolar | 445 | 500 | 600 |  | LCC |  | 345 | 0 | 0.7 | 10% | ++ | ++ | + (between sync areas) | 0 | None |  | 2 | Other | -
635 | Elmed Project | 29 | New interconnection between Italy and Tunisia - new HVDC submarine cable | 12-2028 | 3 | TRUE | Investment on time |  | DCTransmissionLine | Sicily Area (IT) | Mlaaba | DC | Monopolar | 200 | 400 | 600 |  | LCC |  | 850 | 0 | 2.97 | 0% | ++ | ++ | + (between sync areas) | 13 | Other | - | 0 | None
90 | 90 | 33 | Voltage upgrade of the existing 80km Calenzano-Colunga 220kV OHL to 400kV, providing in and out connection to the existing 220/150kV substation of S. Benedetto del Querceto (which already complies with 400kV standards). | 12-2025 | 4 | TRUE | Delayed | Delayed due to permitting reasons. | ACTransmissionLine | Calenzano (IT) | Colunga (IT) | AC | None | 80 | 400 | 0 | 1850 |  |  | 252 | 0 | 0.6 | 0% | ++ | ++ | 0 | 27 | Other | - | 3 | Other
1041 | Rem. lim. in Central Italy | 33 | Removing limitations on existing 220 kV grid between Villanova e S.Barbara | 12-2023 | 4 | FALSE | Ahead of time |  | ACTransmissionLine | Villanova (IT) | S. Barbara (IT) | AC | None | 350 | 220 | 0 | 495 |  |  | 74 | 0 | 0.37 | 0% | ++ | ++ | 0 | 34 | Other | - | 6 | Other | -
313 | Kocin-Mirovka | 35 | Connection of 2 existing 400 kV substations with new double circuit OHL having 120.5 km length and a transmission capacity of 2 x 2445 A. | 10-2028 | 3 | TRUE | Delayed | Delays due to other permit granting reasons | ACTransmissionLine | Kocin (CZ) | Mirovka (CZ) | AC | None | 120.5 | 400 | 0 | 1694 |  |  | 149.772 | 0 | 0.01 | -10%, +15%% |  |  |  | 0.5 | HabitatsDirective None |  | 0.5 | IUCNKeyBiodiversityAreas None |  | In accordance with the European and Czech EIA legislation all over-headline projects (investment items 313 and 315) have undergone screening and full scoping EIA assessment and were granted approval opinion by the competent authority, the Ministry of Environment of the Czech Republic. All investment items are included in the Czech Land Use Development Policy which is the land use plan for the entire country adopted on 15th April 2015 by the Czech government under the governmental resolution. The proposed routes (corridor) of the over-headlines were chosen with respect to the municipalities' land plans, transport and technical infrastructures and other development plans of regional importance (local roads, highways, railways, other transport and technical infrastructures). For the purpose of finding a suitable route, a spatial – land oriented technical studies were carried out that evaluated several route variants with consideration of several aspects including environmental ones. The proposed routes were then communicated with relevant and respective local and regional authorities, municipalities and other technical infrastructure owners. The outputs from the above studies were taken as an important input into the environmental impact assessment which concluded the projects not to have negative NATURA 2000 sites and were granted an EIA approval opinion.
315 | Kocin-Prestice | 35 | Adding second circuit to the existing single circuit OHL with a total transmission capacity of 2 x 2445 A and 117 km length | 12-2028 | 3 | TRUE | Investment on time |  | ACTransmissionLine | Kocin (CZ) | Prestice (CZ) | AC | None | 117 | 400 | 0 | 1694 |  |  | 181.915 | 0 | 0.01 | -10%, +15%% |  |  |  |  | None |  |  |  |  | In accordance with the European and Czech EIA legislation all over-headline projects (investment items 313 and 315) have undergone screening and full scoping EIA assessment and were granted approval opinion by the competent authority, the Ministry of Environment of the Czech Republic. All investment items are included in the Czech Land Use Development Policy which is the land use plan for the entire country adopted on 15th April 2015 by the Czech government under the governmental resolution. The proposed routes (corridor) of the over-headlines were chosen with respect to the municipalities' land plans, transport and technical infrastructures and other development plans of regional importance (local roads, highways, railways, other transport and technical infrastructures). For the purpose of finding a suitable route, a spatial – land oriented technical studies were carried out that evaluated several route variants with consideration of several aspects including environmental ones. The proposed routes were then communicated with relevant and respective local and regional authorities, municipalities and other technical infrastructure owners. The outputs from the above studies were taken as an important input into the environmental impact assessment which concluded the projects not to have negative NATURA 2000 sites and were granted an EIA approval opinion.
650 | BE-LUX-DE Long-Term perspective | 40 | The technical solution is subject to further studies | 12-2040 | 1 | TRUE | Rescheduled |  | OnshoreACTransmissionCable | Aubange (TBC) | LUX-DE (TBC) | AC | None | 16 | 0 | 0 |  |  |  | 210 | 0 | 0.6 | 25%% | ++ | ++ | 0
689 | 689: Vöhringen (DE) - Westtirol (AT) | 47 | Upgrade of an existing over head line to 380 kV, extension of existing and errection of new 380-kV-substations including 380/110-kV-transformers. Transmission route Vöhringen (DE) -Westtirol (AT). This project will increase the current power exchange capacity between the DE, AT. | 12-2030 | 2 | TRUE | Delayed | Scope of the project changed due to technical reasons. | ACTransmissionLine | Vöhringen (DE) | Westtirol (AT) | AC | None | 157 | 380 | 0 |  |  |  | 188 | 0 | 1.49 | 10%% | - | - | 0
462 | 462 | 81 | A new 138 km single circuit 400 kV 1500 MVA OHL from Turleenan 400/275 kV in Northern Ireland to Woodland 400/220 kV in Ireland. This is a new interconnector project between Ireland and Northern Ireland. | 11-2025 | 3 | TRUE | Delayed | Investment delayed due to judicial reviews of planning consent in IE and delayed approval of planning consent in NI. | ACTransmissionLine | Woodland (IE) | Turleenan (NI) | AC | None | 138 | 400 | 0 |  |  |  | 363 | 0 | 0.95 | 20% | ++ | ++ | 0 |  | None |  |  | None
779 | F.Alentejo-Ourique-Tavira | 85 | New double-circuit 400+150 kV OHL F. Alentejo-Ourique-Tavira. The realization of this connection can take advantage of some already existing 150kV single lines, which can be reconstructed as double circuit line 400+150kV. | 02-2023 | 3 | TRUE | Investment on time |  | ACTransmissionLine | F. Alentejo (by Ourique) | Tavira (by Ourique) | AC | None | 122 | 400 | 0 | 1546 |  |  | 60 | 0 | 0.089 | ±10%% |  |  |  | 11 | RAMSARSite
780 | Extension of Ourique substation | 85 | Extension of existing Ourique substation to include 400 kV facilities. | 02-2023 | 3 | TRUE | Investment on time |  | OnshoreSubstation | Ourique (PT) | - | AC | None | 0 | 400 | 0 |  |  |  | 3.9 | 0 | 0.026 | ±10%%
1670 | Alqueva-Divor | 85 | New 75 km single-circuit 400 kV OHL Alqueva-Divor. | 12-2023 | 2 | FALSE | Investment on time |  | ACTransmissionLine | Alqueva | Divor | AC | None | 75 | 400 | 0 | 1546 |  |  | 22 | 0 | 0.066 | ±10%%
1493 | PST Vierraden | 94 | Installation of new PSTs in Vierraden | 11-2025 | 4 | TRUE | Delayed | Due to a court case, an enforceable building permission for the Uckermark-line was delayed. As the court case was settled in July 2022 the upgrade of the Uckermark-line is proceeding. | PhaseShiftingTransformer | Vierraden | Vierraden | AC | None | 0 | 400 | 0 |  |  |  | 110.8 | 0 | 2 | 15%
1488 | Diemen-Lelystad-Ens | 103 | Upgrade of existing 380kV circuits between Diemen, Lelystad and Ens from 2* 2,5 kA to 2* 4kA circuits by replacing the conductors with HTLS conductors | 06-2022 | 4 | TRUE | Rescheduled |  | ACTransmissionLine | Diemen | Ens | AC | None | 75 | 380 | 0 |  |  |  | 105 | 0 | 1 | +/- 10%% | - | - | 0
1490 | Ens-Zwolle | 103 | Upgrade of existing 380kV circuits between Ens and Zwolle from 2* 2,5 kA to 2* 4kA circuits by replacing the conductors with HTLS conductors | 06-2024 | 4 | FALSE | Rescheduled |  | ACTransmissionLine | Ens | Zwolle | AC | None | 32 | 380 | 0 |  |  |  | 41 | 0 | 0.4 | +/- 10%% | - | - | 0
1539 | Krimpen-Geertruidenberg | 103 | Upgrade of existing 380kV circuits between Krimpen and Geertruidenberg from 2* 2,5 kA to 2* 4kA circuits by replacing the conductors with HTLS conductors | 06-2023 | 4 | FALSE | Rescheduled |  | ACTransmissionLine | Krimpen | Geertruidenberg | AC | None | 35 | 380 | 0 |  |  |  | 41 | 0 | 0.4 | +/- 10%% | - | - | 0
1540 | Eindhoven-Maasbracht | 103 | Upgrade of existing 380kV circuits between Eindhoven and Maasbracht from 2* 2,5 kA to 2* 4kA circuits by replacing the conductors with HTLS conductors | 06-2025 | 4 | FALSE | Rescheduled |  | ACTransmissionLine | Eindhoven | Maasbracht | AC | None | 50 | 380 | 0 |  |  |  | 50 | 0 | 0.5 | +/- 10%% | - | - | 0
810 | France Ireland Interconnector | 107 | A new HVDC subsea connection between Ireland and France | 03-2027 | 3 | TRUE | Investment on time |  | OffshoreDCTransmissionCable | Knockraha (IE) | La Martyre (FR) | DC | Monopolar | 575 | 320 | 700 |  | VCS |  | 1000 | 0 | 8.4 | +/- 10%% | ++ | ++ | + (between sync areas) | 33.277 | Other | offshore and onshore sensitivity | 10.072 | Other | offshore and onshore sensitivity
396 | 3rd AC Finland-Sweden north | 111 | Third AC 400 kV overhead line interconnector between Finland north and Sweden SE1. | 12-2025 | 3 | TRUE | Investment on time |  | ACTransmissionLine | Viitajärvi (Finland) | Messaure (Sweden, bidding area SE1) | AC | None | 226 | 400 | 0 | 2200 |  |  | 204 | 0 | 0.15 | +-10%% | ++ | ++ | 0 | 90 5.5 | HabitatsDirective OtherNatureProtectionAreasUnderNationalLaw |  | 10 | MarinStrategyFrameworkDirective
1710 | Viitajärvi-Pyhänselkä | 111 | The investment is a 400 kV overhead line in North Finland. It is part of the 3rd AC cross border project between Finland and Sweden and will enable its full capacity to be utilized. The project will also allow integration of new RES generation at Bothnian bay. | 12-2024 | 3 | FALSE | Investment on time |  | ACTransmissionLine | Viitajärvi | Pyhänselkä | AC | None | 153 | 400 | 0 | 2200 |  |  | 66 | 0 | 0.15 | +-10%% | ++ | ++ | 0
1625 | AC-part of Belgian Modular Offshore Grid II (MOG II) | 120 | One or more offshore substations centralize the production from these offshore wind farms, and then transport it via 220 kV subsea AC cables to the Gezelle 220kV | 03-2028 | 2 | TRUE | Investment on time |  | OffshoreSubstation | Offshore (TBD) | Onshore (TBD | AC | None | 360 | 220 | 2100 |  |  |  | 950 | 0 | 20 | 35%% | ++ | ++ | 0
1791 | DC-part of Belgian Modular Offshore Grid II (MOG II) | 120 | One or more offshore substations centralize the production from these offshore wind farms, and then transport it via +/- 525 kV subsea DC cables to the Gezelle 380kV | 12-2029 | 2 | FALSE | New Investment |  | OffshoreSubstation | Offshore (TBD) | Onshore (TBD | DC | Bipolar | 60 | 1050 | 1400 |  | VCS |  | 750 | 0 | 15 | 35%
934 | Nautilus multi purpose interconnection UK - BE | 121 | This investment item envisions the possibility of a second HVDC connection between UK and Belgian offshore substation (project 120) near the coast. | 12-2030 | 2 | TRUE | Rescheduled |  | OffshoreDCTransmissionCable | Leiston (UK) | MOG2 | DC | Bipolar | 140 | 1050 | 1400 |  | VCS |  | 600 | 0 | 8 | 20%% | ++ | ++ | + (between sync areas) |  | None
373 | Ostroleka-Stanislawow | 123 | Construction of new 400 kV AC double-circuit OHL line with a length of 108 km and capacity of 2x2450 MVA between Ostroleka and Stanislawow. | 12-2023 | 4 | TRUE | Investment on time |  | ACTransmissionLine | Ostroleka (PL) | Stanislawow (PL) | AC | None | 108 | 400 | 0 |  |  |  | 67.74 | 0 | 0.25 | 5%
1783 | Nybro-Hemsjo | 124 | Second phase includes the internal network reinforcements in Sweden to be able to fully utilize the interconnector between Lithuania and Sweden. | 12-2026 | 4 | TRUE | Delayed | Permit recieved. | ACTransmissionLine | Nybro (SE) | Hemsjo (SE) | AC | None | 90 | 400 | 0 |  |  |  | 149 | 0 | 0.1 | +-10%% |  |  |  | 100 100 | BirdsDirective HabitatsDirective
1784 | Ekhyddan-Nybro | 124 | Second phase includes the internal network reinforcements in Sweden to be able to fully utilize the interconnector between Lithuania and Sweden. | 12-2027 | 3 | FALSE | Delayed | Permit denied. Appeal process ongoing | ACTransmissionLine | Ekhyddan (SE) | Nybro (SE) | AC | None | 98 | 400 | 0 |  |  |  | 135 | 0 | 0.1 | +-10%% |  |  |  | 100 100 | HabitatsDirective BirdsDirective
403 | Reinforcements SE2-SE3 in Sweden | 126 | Reactive measures in substations and series compensations in order to increase capacity between SE2 and SE3. Replacement of ageing overhead lines that also will contribute to the increased capacity. The need for capacity is driven by RES integration in northern Sweden and nuclear decommission in southern Sweden. | 01-2035 | 2 | TRUE | Investment on time |  | ReactiveCompensationDevice | Ramsele (SE2) | Hamra (SE3) | AC | None | 1200 | 400 | 0 |  |  |  | 2800 | 0 | 1 | +-10%% | ++ | ++ | 0
86 | New 66km double circuit 400kV OHL between existing Foggia and Villanova 400kV substations, also connected in and out to the Larino and Gissi substations | 127 | New 66km double circuit 400kV OHL between existing Foggia and Villanova 400kV substations, also connected in and out to the Larino and Gissi substations. The section between Villanova and Gissi has already been completed, so the remaining section Gissi - Lartino - Foggia is the main project. | 12-2028 | 3 | TRUE | Delayed |  | ACTransmissionLine | Foggia (IT) | Villanova (IT) | AC | None | 178 | 400 | 0 | 2078 |  |  | 462 | 0 | 0.35 | 0% | ++ | ++ | 0 | 8 | Other | - | 0 | None
96 | New 30km single circuit 400kV OHL between the future substations of Deliceto and Bisaccia, in the Candela area | 127 | New 30km single circuit 400kV OHL between the future substations of Deliceto and Bisaccia, in the Candela area | 05-2022 | 5 | FALSE | Investment on time |  | ACTransmissionLine | Deliceto (IT) | Bisaccia (IT) | AC | None | 30 | 400 | 0 | 2078 |  |  | 209 | 0 | 0.86 | 0% | ++ | ++ | 0 | 22 | Other | - | 0 | None
665 | Wolmirstedt-Isar | 130 | New DC-line to integrate new wind generation from control area 50Hertz especially Mecklenburg-Vorpommern, Brandenburg and Sachsen-Anhalt towards Central/south Europe for consumption and storage. | 12-2025 | 3 | TRUE | Investment on time |  | DCTransmissionLine | Wolmirstedt (DE) | Isar (DE) | DC | Bipolar | 539 | 525 | 2000 |  | VCS |  | 4700 | 0 | 37.6 | +-15%% | ++ | ++ | + (between sync areas) | 78 | OtherNatureProtectionAreasUnderNationalLaw |  | 45 | OtherNatureProtectionAreasUnderNationalLaw
661 | HVDC Line A-North | 132 | New HVDC line from Emden to Osterath to integrate new wind generation especially from North Sea towards Central Germany for consumption. | 12-2027 | 3 | TRUE | Delayed |  | DCTransmissionLine | Emden East (DE) | Osterath (DE) | DC | Bipolar | 300 | 400 | 2400 |  | VCS |  | 2860 | 0 | 22.9 | 10%% |  |  |  | 3.5 16.1 11.0 3.9 2.6 | HabitatsDirective BirdsDirective RAMSARSite IUCNKeyBiodiversityAreas OtherNatureProtectionAreasUnderNationalLaw |  | 28.6 8 | HabitatsDirective MarinStrategyFrameworkDirective
273 | 400kV OHL Cernavoda-Stalpu | 138 | Reinforcement of the cross-section between the Western coast of the Black Sea (Eastern Romania) and the rest of the system. A new 400 kV AC OHL double circuit of 159 km shall be built between the 400 kV substation Cernavoda and the existing 220/110 kV Stalpu substation, which shall be replaced with a 400/110 kV substation (onshore). One of the two circuits shall be connected in-out to the 400 kV substation Gura Ialomitei, situated in the vicinity of the new line. | 12-2022 | 4 | FALSE | Investment on time |  | ACTransmissionLine | Cernavoda (RO) | Stalpu (RO) | AC | None | 159 | 400 | 0 | 1741 |  |  | 76.04 | 1.24 | 0.41 | -5%, +5%% | ++ | ++ | 0 | 1 | HabitatsDirective |  | 0 | None
275 | 400 kV OHL Smardan-Gutinas | 138 | Reinforcement of the cross-section between the Western coast of the Black Sea (Dobrogea area) and the rest of the system. New 400kV double circuit OHL (one circuit wired) between existing substations. Line length 140km. | 12-2024 | 4 | TRUE | Investment on time |  | ACTransmissionLine | Smardan (RO) | Gutinas (RO) | AC | None | 140 | 400 | 0 | 1741 |  |  | 50.32 | 0.84 | 0.25 | -5%, +5%% | ++ | ++ | 0 | 3 | HabitatsDirective |  | 0 | None
715 | 220kV Stalpu substation upgrade to 400 kV | 138 | To reinforce the cross-section between the Black Sea coast wind generation in Romania and Bulgaria and the consumption and storage centers to the West, the 220 kV OHL Stalpu-Teleajen-Brazi is upgraded to 400 kV, as a continuation of the 400 kV d.c. OHL Cernavoda-Stalpu. The 220/110 kV substation Stalpu is upgraded to 400/110kV (1x250MVA). | 12-2024 | 4 | FALSE | Delayed | The contractor responsible for the construction has gone into insolvency | OnshoreSubstation | Stalpu (RO) | Stalpu (RO) | AC | None | 0 | 400 | 0 | 250 |  |  | 15.02 | 0 | 0.15 | -5%, +5%% |  |  |  | 0 | None |  | 0 | None
800 | 400 kV OHL Varna-Burgas | 138 | New 86 km single circuit 400kV OHL in parallel to the existing one. | 08-2021 | 6 | FALSE | Investment on time |  | ACTransmissionLine | Varna(BG) | Burgas(BG) | AC | None | 86 | 400 | 0 |  |  |  | 63 | 0 | 0.8 | +10%, -10%% | ++ | ++ | 0 | 7 | HabitatsDirective
256 | 256 | 142 | New interconnection line BG-GR by a 153km single circuit 400kV OHL. | 06-2022 | 4 | TRUE | Ahead of time |  | ACTransmissionLine | Maritsa East 1 (BG) | N.Santa (GR) | AC | None | 153 | 400 | 0 |  |  |  | 66.24 | 0 | 0.1 | +10%, -10%% | ++ | ++ | 0 | 0.1 4.4 | HabitatsDirective BirdsDirective
257 | 257 | 142 | New 94km single circuit 400kV OHL in parallel to the existing one. | 06-2022 | 6 | FALSE | Investment on time |  | ACTransmissionLine | Maritsa East 1 (BG) | Plovdiv (BG) | AC | None | 94 | 400 | 0 |  |  |  | 57 | 0 | 0.7 | +10%, -10%%
258 | 258 | 142 | New 13km single circuit 400kV OHL in parallel to the existing one. | 03-2021 | 6 | FALSE | Investment on time |  | ACTransmissionLine | Maritsa East 1 (BG) | Maritsa East 3 (BG) | AC | None | 13 | 400 | 0 |  |  |  | 7.4 | 0 | 0.1 | +10%, -10%%
262 | 262 | 142 | New 400kV OHL. Line lengt 145km. | 03-2021 | 6 | FALSE | Investment on time |  | ACTransmissionLine | Maritsa East 1 (BG) | Burgas (BG) | AC | None | 145 | 400 | 0 |  |  |  | 80 | 0 | 1.1 | +10%, -10%%
238 | New_400 kV OHL RO-RS | 144 | New 131 km double circuit 400kV OHL between Romania and Serbia (63 km on Romanian (thermal limit 2513 A) side and 68 km on Serbian (thermal limit 1920 A) side). | 12-2025 | 6 | TRUE | Delayed | Due to some delays related to investments 701 and 269 the line is not operated | ACTransmissionLine | Resita (RO) | Pancevo (RS) | AC | None | 131 | 400 | 0 | 1741 |  |  | 47 | 1.02 | 0.23 | -5%, +5%% | ++ | ++ | 0 | 1 | HabitatsDirective |  | 0 | None
269 | 400 kV OHL Portile de Fier-Resita | 144 | New 116 km 400kV OHL single circuit between existing substation 400 kV Portile de Fier and new 400 kV substation Resita. | 12-2024 | 4 | FALSE | Investment on time |  | ACTransmissionLine | Portile de Fier (RO) | Resita (RO) | AC | None | 116 | 400 | 0 | 1741 |  |  | 28.05 | 0.7 | 0.14 | -5%, +5%% | ++ | ++ | 0 | 30 | HabitatsDirective |  | 0 | None
270 | Upgrade of the existing 220kV double circuit OHL Resita -Timisoara - Sacalaz to 400kV | 144 | Upgrade of an existing 220 kV AC double circuit line (OHL) between Resita - Timisoara (RO) to 400 kV double circuit line Resita-Timisoara/Sacalaz of which: 74 km from Resita to Timisoara and 92 km from Resita to Sacalaz , both overhead lines will be built on common towers up to Icloda on 58 km. | 12-2026 | 3 | FALSE | Rescheduled |  | ACTransmissionLine | Resita (RO) | Timisoara-Sacalaz (RO) | AC | None | 166 | 400 | 0 | 1741 |  |  | 46.93 | 1 | 0.23 | -5%, +5%% | ++ | ++ | 0 | 17.5 | HabitatsDirective |  | 0 | None
701 | 400 kV Substation Resita | 144 | New 400 kV substation Resita (T400/220 kV 400 MVA + T 400/110 kV 250 MVA), as development of the existing 220/110 kV substation. | 12-2025 | 4 | FALSE | Investment on time |  | OnshoreSubstation | Resita (RO) | Resita (RO) | AC | None | 0 | 400 | 0 | 0 |  |  | 23.26 | 0 | 0.23 | -5%, +5%% |  |  |  | 0 | None |  | 0 | None
705 | 400 kV Substation Timisoara | 144 | Completion of 220 kV substation Timisoara and partially replacement with 400 kV substation (2x250 MVA 400/110 kV) | 12-2026 | 4 | FALSE | Delayed | Long duration of the procurement procedure, delays due to executor and pandemic impact of COVID 19 | OnshoreSubstation | Timisoara (RO) | Timisoara (RO) | AC | None | 0 | 400 | 0 |  |  |  | 18.02 | 0 | 0.18 | -5%, +5%% |  |  |  | 0 | None |  | 0 | None
1827 | Upgrade of the existing 220kV double circuit OHL Arad -Timisoara - Sacalaz to 400kV | 144 | Upgrade of the existing 220 kV AC double circuit line (OHL) Arad-Timisoara/Sacalaz to 400 kV on 67 km of which: 14 km of line will be build single circuit between Sacalaz-C.Aradului-""connection point"", 11 km single circuit from Timisoara to ""connection point"" and the rest 42 km of the line will be double circuit from ""connection point"" to Arad. The investment contains also the 400/110kV substation Sacalaz and the extension of substation 400kV Arad. | 12-2029 | 3 | FALSE | Rescheduled |  | ACTransmissionLine | Arad(RO) | Timisoara-Sacalaz(RO) | AC | None | 109 | 400 | 0 | 1741 |  |  | 50.39 | 0.65 | 0.38 | -5%,+5%% |  |  |  | 17 | HabitatsDirective
616 | Salgareda - Bericevo | 150 | New HVDC link between Salgareda (IT) and Bericevo/Divaca (SI) | 12-2042 | 1 | TRUE | Delayed | Project under consideration on SI side (permitting not started yet in Slovenia) | DCTransmissionLine | Salgareda (IT) | Bericevo (SI) | DC | None | 0 | 500 | 1000 |  | VCS |  | 755 | 0 | 4 | 15% | ++ | ++ | + (between sync areas) | 169 2 | OtherNatureProtectionAreasUnderNationalLaw Other | - | 174 2 | OtherNatureProtectionAreasUnderNationalLaw Other | -
987 | France-Alderney-Britain | 153 | France-Alderney-Britain (FAB) is a new 220km-long HVDC subsea interconnection between Exeter (UK) and Menuel (France) with VSC converter station at both ends. Expected rated capacity is 1250 MW. | 12-2030 | 3 | TRUE | Delayed | Delayed due to uncertainty of regulatory decisions | OffshoreDCTransmissionCable | Menuel (FR) | Exeter (GB) | DC | Monopolar | 220 | 320 | 1250 |  | VCS |  | 1000 | 0 | 7.6 | +/- 27%% | ++ | ++ | + (between sync areas) | 10 | HabitatsDirective |  | 0 | None
382 | New 330 kV OHL Vilnius-Neris | 170 | New 330 kV OHL Vilnius-Neris. 57,9 km will be constructed as new line and 22,8 km will be used part of exicting 330 kV OHL Vilnius-Molodecno (Vilnius-Molodecno will be disconnected until end of 2025). | 12-2025 | 3 | FALSE | Investment on time |  | ACTransmissionLine | Vilnius | Neris | AC | None | 80 | 330 | 0 | 1097 |  |  | 24.76 | 0.09 | 0.14 | +5%, - 5%% | ++ | ++ | 0
1010 | 330 kV OHL Tartu-Valmiera | 170 | Reinforcement of existing 330 kV OHL. The investment is also a backbone for Baltics Synchronization with CESA. On Estonian territory parallel 110 kV lines will be installed on the common tower (approx. 51 km) to reduce social and environmental impact. | 12-2025 | 4 | FALSE | Ahead of time |  | ACTransmissionLine | Tartu (EE) | Valmiera (LV) | AC | None | 133 | 330 | 0 | 1772 |  |  | 30.66 | 0 | 0.094 | +5%, - 5%% |  |  |  | 0.3 | OtherNatureProtectionAreasUnderNationalLaw
1011 | Valmiera -Tsirguliina 330 kV | 170 | Reinforcement of existing 330 kV OHL. The investment is also a backbone for Baltics Synchronization with CESA | 12-2025 | 3 | FALSE | Investment on time |  | ACTransmissionLine | Tsirguliina (EE) | Valmiera (LV) | AC | None | 60 | 330 | 0 | 1770 |  |  | 22 | 0 | 0.13 | +5%, - 5%% | [6 empty] | 0.6 | HabitatsDirective
1012 | 330 kV OHL Tartu-Balti (L300) | 170 | Reinforcement of existing 330 kV OHL between Balti and Tartu 330 kV substations in Estonia. Old 330 kV line will be replaced with new one with a conductor 3x400 mm2 in phase. The thermal capacity of the line is planned 2400A @ wire max operating temperature 80 degrees celsius. The investment is also a backbone for Baltics Synchronization with CESA (project nr 170). Parallel 110 kV lines will be installed on the common towers along the whole length of the line corridor (approx. 132 km) to reduce social and environmental impact. | 12-2023 | 3 | FALSE | Ahead of time |  | ACTransmissionLine | Balti | Tartu | AC | None | 132 | 330 | 0 | 1770 |  |  | 51.2 | 0 | 0.11 | +5%, - 5%% |  |  |  | 1.4 3.3 | BirdsDirective OtherNatureProtectionAreasUnderNationalLaw |  | 0.5 | HabitatsDirective
1013 | Viru-Tsirguliina 330kV OHL | 170 | Reinforcement of existing 330 kV OHL between Viru and Tsirguliina 330 kV substations in Estonia. Old 330 kV line will be replaced with new one with a conductor 3x400 mm2 in phase. The thermal capacity of the line is planned 2400A @ wire max operating temperature 80 degrees celsius. The investment is also a backbone for Baltics Synchronization with CESA (project nr 170). Parallel 110 kV lines will be installed on the common tower (approx. 14 km) to reduce social and environmental impact. To optimize line lenght and reactive power compensation a new 330 kV substation (named Mustvee) will be constructed in the middle of the power line. | 12-2025 | 3 | FALSE | Rescheduled | During the planning and design process since last TYNDP 2020 the exact construction and outage schedule was specified and coordinated and therefore the line reconstruction schedule was also changed. Planned commissioning in October-November 2025. Planned construction starts June 2023. | ACTransmissionLine | Viru | Tsirguliina | AC | None | 244 | 330 | 0 | 1770 |  |  | 73.2 | 0 | 0.17 | +5%, - 5%% |  |  |  | 4.7 | OtherNatureProtectionAreasUnderNationalLaw |  | 0.6 | HabitatsDirective
1034 | New HVDC interconnector "Harmony Link" | 170 | New HVDC subsea cable connection between Lithuania and Poland. The project includes HVDC submarine and land cable system and converter stations at each end. | 01-2026 | 3 | TRUE | Investment on time |  | OffshoreDCTransmissionCable | Darbenai | Zarnowiec | DC | Bipolar | 330 | 300 | 700 |  | VCS |  | 682.6 | 0 | 10.24 | +5%, - 5%% | ++ | ++ | + (between sync areas) | 0.01 7.8 144.4 7.8 | HabitatsDirective BirdsDirective MarinStrategyFrameworkDirective OtherNatureProtectionAreasUnderNationalLaw
1118 | Further infrastructure aspects related to the implementation of the synchronisation of the Baltic States’ system with the continental European network | 170 | Further infrastructure aspects ‘not-known-today’ related to the implementation of the synchronisation of the Baltic States’ system with the continental European Network arising from ongoing synchronisation studies. | 12-2025 | 1 | FALSE | Investment on time |  |  | - | - | AC | None | 0 | 330 | 0 |  |  |  | 186.9 | 0 | 1.87 | +5%, - 5%%
1565 | Reconstruction of 330 kV OHL LE-Vilnius | 170 | Reconstruction of 330 kV OHL LE-Vilnius from single-circuit into double-circuit line. | 11-2020 | 6 | FALSE | Investment on time |  | ACTransmissionLine | Lietuvos E | Vilnius | AC | None | 41 | 330 | 0 | 789 |  |  | 18.281 | 0 | 0.071 | +5%, - 5%% | ++ | ++ | 0
1566 | Reconstructions in North Eastern Lithuania | 170 | Reconstruction of 330 kV Utenos and 330 kV Ignalinos AE substations. Relocation of HV equipment (from 330/110/10 kV Ignalinos AE substation to 330/110/10 kV Lietuvos E substation) and changing topology of 330 kV overhead lines. | 12-2021 | 6 | FALSE | Investment on time |  | OnshoreSubstation | Utena | Ignalinos AE | AC | None | 0 | 330 | 0 |  |  |  | 22.85 | 0 | 0.23 | +5%, - 5%%
1568 | Upgrades in Alytus substation (LT) | 170 | Construction of three new 400/330 kV autotransformers in Alytus substation, to connect Lithuania and Poland transmission systems in AC mode. | 12-2021 | 6 | FALSE | Investment on time |  | Transformer | Alytus | - | AC | None | 0 | 400 | 0 |  |  |  | 22.438 | 0 | 0.22 | +5%, - 5%%
1571 | New Voltage stabiliser units (SVC), Battery Energy Storage System (BESS) control units in Lithuania, Latvia and Estonia. | 170 | If Studies concerning not known today further infrastructure aspects related to the implementation of the synchronisation of the Baltic States’ system with the continental European network, identify the necessity to install additional SVC. New Battery Energy Storage System (BESS) units - for frequency regulation (FCR and FRR) and to ensure power system secure and stable operation. | 12-2025 | 4 | FALSE | Investment on time |  | ReactiveCompensationDevice | - | - | AC | None | 0 | 0 | 0 |  |  |  | 138 | 0 | 1.38 | +5%, - 5%% | + | + | 0
1572 | Monitoring and control system upgrades in Lithuania, Latvia and Estonia. Upgrading control systems of exicting HVDC connections (EstLink 1 and EstLink 2 and NordBalt). | 170 | Upgrade of PSS in power stations. AGC impementation and commissioning in SCADA systems and power plants. WAMS and WAMPAC systems. Upgrade of instrument transformers and metering system in transmission network and is necessary to provide stable metering system during synchronous operation with Continental Europe or during island operation in emergency cases. System upgrades (automatics modernisation), SCADA and dispatcher trainer. In order to ensure system stability after high sudden power imbalance during BSPS island operation, activation of fast frequency reserves within view milliseconds via HVDC’s links is crucial. For this project is necessary to perform research, modelling and upgrading control system of HVDC's. | 12-2025 | 2 | FALSE | Investment on time |  |  | - | - | AC | None | 0 | 0 | 0 |  |  |  | 43.2 | 0 | 0.432 | +5%, - 5%%
1632 | New 330 kV Musa substation | 170 | New 330 kV Musa substation. The new substation will create switching capability at the junction of overhead lines Siauliai-Kaunas, Siauliai-Viskali, and Siauliai-Telsiai, which will improve general availability, resilience and throughput of the grid to support synchronization. The project includes territorial planning, land acquisition, procurement, design and construction phases. | 12-2025 | 3 | FALSE | Investment on time |  | OnshoreSubstation | Musa | - | AC | None | 0 | 330 | 0 |  |  |  | 6.14 | 0 | 0.06 | +5%, - 5%%
1634 | New 330 kV OHL Bitenai - KHAE | 170 | New 330 kV OHL Bitenai-KHAE. One part of the new line will be constructed as second circuit on exicting 330 kV OHL Bitenai-Jurbarkas (39 km), one part will be new line (63 km), and as third part of new line will be used part of exicting 330 kV OHL KHAE-Sovetsk (KHAE-Sovetsk will be disconnected until end of 2025). | 10-2025 | 3 | FALSE | Investment on time |  | ACTransmissionLine | Bitenai | KHAE | AC | None | 211 | 330 | 0 | 789 |  |  | 42.06 | 0 | 0.367 | +5%, - 5%% | ++ | ++ | 0
1659 | New 330 kV OHL Darbenai-Bitenai | 170 | New 330 kV OHL Darbenai-Bitenai. One part of the new line will be constructed as second circuit on existing 330 kV OHL Grobine-Klaipeda (45,5 km), second part will be new line (12,1 km), third part will be constructed as second circuit on existing 330 kV OHL Klaipeda-Sysa-Bitenai (79,5 km). | 07-2025 | 3 | FALSE | Investment on time |  | ACTransmissionLine | Darbenai | Bitenai | AC | None | 137 | 330 | 0 | 960 |  |  | 62.77 | 0 | 0.239 | +5%, -5%% | ++ | ++ | 0 | 10.38 | OtherNatureProtectionAreasUnderNationalLaw
1660 | New 330 kV Darbenai substation | 170 | New 330 kV Darbenai substation, necessary for the connection of the new 330 kV line Darbenai-Bitenai (inv. 1659), as well as new HVDC subsea cable known as Harmony Link (inv.1034) and offshore wind farm (project 1042). This project includes territory planning, land acquisition and construction phases. | 03-2025 | 3 | FALSE | Investment on time |  | OnshoreSubstation | Darbenai | - | AC | None | 0 | 330 | 0 |  |  |  | 15.16 | 0 | 0.15 | +5%, - 5%%
1661 | Construction of new 400kV line Dunowo-Zydowo Kierzkowo | 170 | Dunowo-Zydowo Kierzkowo 400kV line is necessary to assure that after commissioning of Harmony Link and offshore wind farms, full capabilities would be available on the Polish-Lithuanian subsea interconnector. This project includes reconstruction of Dunowo substation with installation of 400/110 kV transformers and construction of new double-circuit 400 kV. | 12-2025 | 3 | FALSE | New Investment |  | ACTransmissionLine | Dunowo | Zydowo Kierzkowo | AC | None | 57.11 | 400 | 0 |  |  |  | 46.57 | 0 | 0.11 | +5%, -5%% | ++ | ++ | 0
1662 | Construction of new 400kV line Pila Krzewina-Zydowo Kierzkowo | 170 | Pila Krzewina-Zydowo Kierzkowo 400kV line is interrelated with project aiming in building Dunowo-Zydowo Kierzkowo line. This project includes reconstruction and modernization of Pila Krzewina electrical station with installation of 400/110 kV transformers and reactive power compensation devices and construction of new double-circuit 400 kV. | 12-2025 | 3 | FALSE | New Investment |  | ACTransmissionLine | Pila Krzewina | Zydowo Kierzkowo | AC | None | 119 | 400 | 0 |  |  |  | 127.15 | 0 | 0.22 | +5%, -5%% | ++ | ++ | 0
1663 | Modernization of 400kV OHL Krajnik-Morzyczyn | 170 | To allow effective energy flows in the north-west part of Poland after commissioning of Harmony Link, modernization of “North Line” (line between Krajnik and Gdansk Blonia) is necessary. The first project of North Line is modernization of Krajnik-Morzyczyn 400kV line. | 07-2023 | 4 | FALSE | New Investment |  | ACTransmissionLine | Krajnik | Morzyczyn | AC | None | 41.5 | 400 | 0 |  |  |  | 0.854 | 0 | 0.04 | +5%, -5%%
1664 | Modernization of 400kV OHL Morzyczyn-Dunowo-Slupsk-Zarnowiec | 170 | Modernisation of Morzyczyn-Dunowo-Slupsk-Zarnowiec 400kV line would be the longest part included in modernization of North Line. Because of its length this project consists of three sections: Modernization of Morzyczyn-Dunowo 400 kV, Modernization of Dunowo-Slupsk 400 kV, Modernization of Slupsk-Zarnowiec 400 kV. | 12-2023 | 2 | FALSE | New Investment |  | ACTransmissionLine | Morzyczyn | Zarnowiec | AC | None | 288.5 | 400 | 0 |  |  |  | 13.52 | 0 | 0.3 | +5%, -5%%
1665 | Modernization of 400kV OHL Zarnowiec-Gdansk/Gdansk Przyjazn-Gdansk Blonia | 170 | Modernisation of Zarnowiec-Gdansk/Gdansk Przyjazn-Gdansk Blonia 400kV line would be the last part included in modernization of North Line. | 12-2023 | 2 | FALSE | New Investment |  | ACTransmissionLine | Zarnowiec | Gdansk Blonia | AC | None | 77 | 400 | 0 |  |  |  | 4.53 | 0 | 0.1 | +5%, -5%%
1669 | Synchronous condensers in Lithuania, Latvia and Estonia | 170 | Synchronous condensers providing inertia, voltage stability, frequency stability and short-circuit power in Lithuania, Latvia and Estonia. | 12-2025 | 3 | FALSE | Investment on time |  | ReactiveCompensationDevice | 330 kV substations in the Baltics | - | AC | None | 0 | 0 | 0 |  |  | -1170 | 253.584 | 0 | 2.54 | +5%, - 5%% | + | ++ | ++
1702 | Common Baltic Frequency Stability Assessment System (FSAS). Modernisation of System Protection Schemes (SPS) and Under Frequency Load Shedding (UFLS). | 170 | FSAS is a common Baltic IT platform, necessary to ensure frequency monitoring in Baltic system, in order to ensure frequency stability in the region in synchronous mode with the CEN and in izolated mode after incidents. | 06-2025 | 2 | FALSE | New Investment |  | OnshoreSubstation | - | - | AC | None | 0 | 0 | 0 |  |  |  | 11.4 | 0 | 0.114 | +5%, - 5%%
1703 | Reconstruction of shunt reactors switchgears | 170 | Due to the synchronisation project the total length of the power lines will increase. Increase in the total length of power lines higher reactive power generation by these lines. In order to reduce the risk that the voltages will rise too high, sufficient amount of reactive power compensation is needed, which can be achieved with the existing shunt reactors. Nevertheless, the shunt reactors need reliable switchgear to help to minimise the risk induced by commutation errors. | 12-2025 | 2 | FALSE | New Investment |  | OnshoreSubstation | Aruküla, Balti, Harku, Kiisa, Paide, Rakvere, Sindi substations | Aruküla, Balti, Harku, Kiisa, Paide, Rakvere, Sindi substations | AC | None | 0 | 330 | 0 |  |  |  | 4.3 | 0 | 0.01 | +5%, - 5%%
1014 | Greenconnector | 174 | Greenconnector is an HVDC interconnector project between Italy and Switzerland for power transport using DC cables rather than overhead lines. The route length is about 165 km. The design power is 1000 MW (1200 MW in overload condition), while the DC voltage is +/- 400 kV DC. Two cables will be installed, working with a bipolar scheme. Great part of the cables route will exploit a section of an existing oil pipeline, no longer in service since January 1997. This pipeline crosses the Italian and Switzerland border at Splgenpass and is running close by the two end stations of the Greenconnector project (Bonaduz in Graubunden Canton and Verderio Inferiore, Lecco). The cables will be pulled inside the pipeline itself, reducing the amount of civil works required before and after cable laying and therefore limiting even temporary environmental impact. For about 47 km the cables will run across the Como lake. | 12-2026 | 3 | TRUE | Delayed | Negotiations with the Swiss authorities are in progress and advancing | DCTransmissionLine | Verderio | Bonaduz | DC | Bipolar | 165 | 400 | 1000 |  | VCS |  | 660 | 20 | 2 | -10 / +15 %% | ++ | ++ | + (between sync areas) | 7.9 4.4 | HabitatsDirective HabitatsDirective |  | 4.7 | IUCNKeyBiodiversityAreas |  | The project avoids the dismatling of about 80 km of an existing oil pipeline no longer in use. The pipeline crosses very sensitive environmental areas (In particular the protected areas mentioned for the Residual environmental and social impacts and mountain areas). Should the pipeline be dismissed, the estimated costs add up to about 25 million euros (supporting documents are available upon request). So our project generates a positive residual impact equal to such amount.
995 | Hansa PowerBridge I | 176 | New HVDC interconnector between Sweden (SE4) and Germany (50 Hertz) aiming to enhance the integration of the Nordic and the continental power market. Moreover the interconnector facilitates RES integration and increases the system adequacy in both systems. | 12-2026 | 3 | TRUE | Investment on time |  | OffshoreDCTransmissionCable | Hurva (SE4) | Guestrow (DE) | DC | Monopolar | 300 | 300 | 700 |  | VCS |  | 660 | 0 | 1 | +-10 %% | ++ | ++ | + (between sync areas) | 23 20 30 10 | HabitatsDirective OtherNatureProtectionAreasUnderNationalLaw OtherNatureProtectionAreasUnderNationalLaw BirdsDirective |  | 30 30 | IUCNKeyBiodiversityAreas MarinStrategyFrameworkDirective |  | Tourist area with protected biotopes, water protection areas: 4 km
1018 | DKW-DE, Westcoast, TYNDP ID 183.1018 | 183 | New 380 kV line DKW-DE between Klixbuell (DE) and Endrup (DKW) as part of connection Endrup-Brunsbüttel | 12-2023 | 3 | TRUE | Investment on time |  | ACTransmissionLine | Klixbüll (DE) | Endrup (DKW) | AC | None | 92 | 380 | 0 |  |  |  | 210 | 0 | 2 | 10% |  |  |  | 5 | OtherNatureProtectionAreasUnderNationalLaw
886 | 886 - east of Austria | 186 | To allow the grid integration of the planned renewable energy generation (mainly wind power) in the north-eastern part of Austria ("Weinviertel") and to cover the foreseen load growth in that region the transmission grid infrastructure has to be enforced and new substations for the connection needs to be erected | 12-2022 | 4 | TRUE | Investment on time |  | ACTransmissionLine | Seyring | Zaya | AC | None | 60 | 380 | 0 |  |  |  | 213 | 0 | 0.64 | 10% | [6 empty] | 31 | None
997 | 997 Pleinting - St. Peter | 187 | new 380-kV-line Pleinting (DE) - St. Peter (AT) on exting OHL corridor | 12-2030 | 3 | TRUE | Investment on time |  | ACTransmissionLine | Pleinting (DE) | St. Peter (AT) | AC | None | 60 | 380 | 0 |  |  |  | 212.9 | 0 | 1.7 | 10% | [6 empty] | 2 | OtherNatureProtectionAreasUnderNationalLaw
1382 | NorthConnect | 190 | A 665 km long subsea interconnector between Norway and Scotland is planned to be realized in 2024. The main driver for the project is to integrate the hydro-based Norwegian system with the thermal/nuclear/wind-based British system. The interconnector will improve security of supply both in Norway in dry years and in Great Britain in periods with negative power balance (low wind, low solar, high demand etc.). Additionally the interconnector will be positive both for the European market integration, for facilitating renewable energy and also for preparing for a power system with lower CO2-emissions. The interconnector is planned to be a 500 kV 1400 MW HVDC subsea interconnector between western Norway and eastern Scotland. | 12-2027 | 1 | TRUE | Delayed | Permitting process in Norway | OffshoreDCTransmissionCable | Sima | Peterhead | DC | Monopolar | 665 | 500 | 1400 |  | VCS |  | 1675 | 1700 | 10 | Costs are based on feedback from the supply chain; CAPEX same as previous input to ENTSO-E, and OPEX adjusted from 30 to 10.%
308 | Vernerov-Vitkov | 200 | New 400 kV double circuit OHL with a transmission capacity of 2 x 2445 A and 83 km length. | 06-2024 | 3 | TRUE | Investment on time |  | ACTransmissionLine | Vernerov (CZ) | Vitkov (CZ) | AC | None | 83 | 400 | 0 | 1694 |  |  | 136.87 | 0 | 0.06 | -10%, +15%% |  |  |  | 35 9 | BirdsDirective HabitatsDirective None |  | 15 | IUCNKeyBiodiversityAreas None |  | In accordance with the European and Czech EIA legislation all over-headline projects (investment items 308, 309 and 314) have undergone screening and full scoping EIA assessment and were granted approval opinion by the competent authority, the Ministry of Environment of the Czech Republic. All investment items are included in the Czech Land Use Development Policy which is the land use plan for the entire country adopted on 15th April 2015 by the Czech government under the governmental resolution. The proposed routes (corridor) of the over-headlines were chosen with respect to the municipalities' land plans, transport and technical infrastructures and other development plans of regional importance (local roads, highways, railways, other transport and technical infrastructures). For the purpose of finding a suitable route, a spatial – land oriented technical studies were carried out that evaluated several route variants with consideration of several aspects including environmental ones. The proposed routes were then communicated with relevant and respective local and regional authorities, municipalities and other technical infrastructure owners. The outputs from the above studies were taken as an important input into the environment impact assessment which concluded the projects not to have negative NATURA 2000 sites and were granted an EIA approval.
1380 | Würmlach (AT) - Somplago (IT) interconnection | 210 | "Wurmlach (AT) – Somplago (IT) Interconnection is a cross-border electrical line promoted by Alpe Adria Energia Srl. The project concerns a 220kV a.c. merchant line, 300 MW thermal capacity from Somplago substation to new Wurmlach substation, including a Phase Shifter Transformer located in Austria" | 01-2026 | 3 | TRUE | Delayed | PERMITTING - Delays due to environmental problems (including re-routing) and delay of EIA assessment due to change of EIA Commission (2019) | ACTransmissionLine | SOMPLAGO | WURMLACH | AC | None | 51 | 220 | 0 | 300 |  |  | 88.1 | 3.84 | 0.8 | 7%% | ++ | ++ | 0 | 2.2 2.2 | HabitatsDirective BirdsDirective None |  | 0.1 | BirdsDirective
1407 | EuroAsia Interconnector | 219 | The EuroAsia Interconnector consists of a 500 kV DC underwater electric cable and any essential equipment and/or installation for interconnecting the Cypriot, Israeli and the Greek transmission networks (offshore). The Interconnector will have a capacity of 2000 MW and a total length of around 820 nautical miles/around 1200 km (approx. 329 km between CY and IL, 879 km between CY and Crete) and allow for reverse transmission of electricity. | 12-2026 | 3 | TRUE | Delayed | The National Regulatory Authorities of Greece and Cyprus approved the submitted Investment Request for the Project and agreed on the CBCA between them. The decision "Cross-Border Cost Allocation Between the Hellenic Regulatory Authority for Energy (RAE) and the Cyprus Energy Regulatory Authority (CERA)" provided on 10th of October 2017 concerned the implementation of PCIs 3.10.2 & 3.10.3. With the corresponding decision for PCI 3.10.1 not yet received, and to avoid delays in the implementation of the Project and to be in line with the obligations and commitments arising from the CBCA approval, the Project Promoter decided to amend the order of implementation of the three PCIs consisting PCI 3.10 as follows, with PCIs 3.10.2 & 3.10.3 implemented concurrently: PCI 3.10.3 Interconnection between Korakia, Crete and Attica region(EL) PCI 3.10.2 Interconnection between Kofinou (CY) and Korakia, Crete (EL) PCI 3.10.1 Interconnection between Hadera (IL) and Kofinou (CY). The CBCA has been updated on 23.04.2021 | OffshoreDCTransmissionCable | Hadera Site | Kofinou Site | DC | Bipolar | 325 | 500 | 1040 |  | VCS |  | 790 | 0 | 7.9 | 10%
1409 | EuroAsia Interconnector | 219 | The Euro Asia Interconnector consists of a 500 kV DC underwater electric cable and any essential equipment and/or installation for interconnecting the Cypriot, Israeli and the Greek transmission networks (offshore). The Interconnector will have a capacity of 2000 MW and a total length of around 820 nautical miles/around 1200 km (approx. 329 km between CY and IL, 879 km between CY and Crete) and allow for reverse transmission of electricity. | 12-2026 | 3 | TRUE | Delayed | The National Regulatory Authorities of Greece and Cyprus approved the submitted Investment Request for the Project and agreed on the CBCA between them. The decision "Cross-Border Cost Allocation Between the Hellenic Regulatory Authority for Energy (RAE) and the Cyprus Energy Regulatory Authority (CERA)" provided on 10th of October 2017 concerned the implementation of PCIs 3.10.2 & 3.10.3. With the corresponding decision for PCI 3.10.1 not yet received, and to avoid delays in the implementation of the Project and to be in line with the obligations and commitments arising from the CBCA approval, the Project Promoter decided to amend the order of implementation of the three PCIs consisting PCI 3.10 as follows, with PCIs 3.10.2 & 3.10.3 implemented concurrently: PCI 3.10.3 Interconnection between Korakia, Crete and Attica region(EL) PCI 3.10.2 Interconnection between Kofinou (CY) and Korakia, Crete (EL) PCI 3.10.1 Interconnection between Hadera (IL) and Kofinou (CY). The CBCA has been updated on 23.04.2021 | OffshoreDCTransmissionCable | Kofinou Site | Korakia (Crete)Site | DC | Bipolar | 921 | 500 | 1000 |  | VCS |  | 1575 | 0 | 15.6 | 10%
1107 | 2nd interconnecter between Belgium and Germany | 225 | This investment item envisions the possibility of a second 1 GW HVDC interconnection between Belgium and Germany. Subject to further studies. | 12-2038 | 1 | TRUE | Rescheduled |  | DCTransmissionLine | Gramme (BE) | Dahlem (DE) | DC | Monopolar | 150 | 660 | 1000 |  | VCS |  | 600 | 0 | 4.8 | 20%% | ++ | ++ | + (between sync areas)
627 | 400 kV interconnection RS-BA | 227 | Description of broader context - New double circuit 400 kV OHL connecting existing substation Pljevlja (ME) and substation Bajina Basta (RS) and new double circuit 400kV OHL connecting existing substation Visegrad (BA) and substation Bajina Basta (RS). In the first phase one 400 kV circuit would be equiped. In the second phase New SS Bistrica (RS) would be connected to the exisitng double circuit 400 kV OHL between SS Bajina Basta (RS), SS Visegrad (BA) and SS Pljevlja (ME). Part of regional transmission corridor northeast-southwest. | 09-2026 | 3 | TRUE | Investment on time |  | ACTransmissionLine | SS Bajina Basta | SS Visegrad | AC | None | 45.2 | 400 | 0 | 1330 |  |  | 19.6 | 0 | 0.2 | 5% | ++ | ++ | 0 | 17 | OtherNatureProtectionAreasUnderNationalLaw |  | 1 | MarinStrategyFrameworkDirective
628 | 2x400 kV OHL B.Basta-Obrenovac | 227 | Double circuit 400 kV OHL between upgraded substation Bajina Basta and substation Obrenovac. Part of larger regional transmission corridor northeast-southwest. | 09-2025 | 3 | FALSE | Delayed | The investment suffered a one-year delay compared to the previous TYNDP due to the negotiations for closing the financial structure (grants, loans and own funds). | ACTransmissionLine | SS Bajina Basta | SS Obrenovac | AC | None | 109 | 400 | 0 | 2660 |  |  | 44.6 | 0 | 0.45 | 5% | ++ | ++ | 0
630 | 400 kV interconnection RS-ME | 227 | Description of broader context - New double circuit 400kV OHL connecting existing substation Pljevlja (ME) and substation Bajina Basta (RS) and new double circuit 400kV OHL connecting existing substation Visegrad (BA) and substation Bajina Basta (RS). In the first phase one 400 kV circuit would be equiped. In the second phase New SS Bistrica (RS) would be connected to the exisitng double circuit 400 kV OHL between SS Bajina Basta (RS), SS Visegrad (BA) and SS Pljevlja (ME). Part of regional transmission corridor northeast-southwest. | 09-2026 | 3 | TRUE | Investment on time |  | ACTransmissionLine | SS Bajina Basta | SS Pljevlja | AC | None | 98.4 | 400 | 0 | 1330 |  |  | 43.8 | 0 | 0.44 | 5% | ++ | ++ | 0 | 17 | OtherNatureProtectionAreasUnderNationalLaw |  | 1 | MarinStrategyFrameworkDirective
631 | Upgrading SS Bajina Basta to 400 kV voltage level | 227 | Upgrade of existing 220/110 kV substation in Bajina Basta to 400/220/110 kV substation as part of overall western Serbia system upgrade to 400 kV voltage level. Part of larger regional transmission corridor northeast-southwest. | 09-2025 | 3 | FALSE | Delayed | The investment suffered a one-year delay compared to the previous TYNDP due to the negotiations for closing the financial structure (grants, loans and own funds). | OnshoreSubstation | Bajina Basta (RS) | Bajina Basta (RS) | AC | None | 0 | 400 | 0 |  |  |  | 14.35 | 0 | 0.14 | 5%
1526 | 400 kV OHL Lastva - Pljevlja | 227 | 400 kV OHL Lastva - Pljevlja | 09-2022 | 4 | FALSE | Delayed | Adjusted to match the remainder of the project. | ACTransmissionLine | SS Lastva | SS Pljevlja | AC | None | 151 | 400 | 0 | 1385 |  |  | 70.2 | 0 | 0.7 | 5% | ++ | ++ | 0
1527 | 400 kV OHL SS Kragujevac 2 - SS Kraljevo 3 | 227 | 400 kV OHL SS Kragujevac 2 - SS Kraljevo 3 | 09-2022 | 4 | FALSE | Delayed | Slightly delayed due to the long contractor choice process. | ACTransmissionLine | SS Kragujevac 2 | SS Kraljevo 3 | AC | None | 59.4 | 400 | 0 | 1330 |  |  | 16 | 0 | 0.16 | 2% | ++ | ++ | 0 |  |  |  | 2 | MarinStrategyFrameworkDirective
1528 | Upgrade of SS Kraljevo 3 to 400 kV voltage level | 227 | Upgrade of SS Kraljevo 3 to 400 kV voltage level. | 09-2022 | 4 | FALSE | Delayed | Slightly delayed due to the long contractor choice process. | OnshoreSubstation | SS Kraljevo 3 | SS Kraljevo 3 | AC | None | 0 | 400 | 0 |  |  |  | 13.6 | 0 | 0.14 | 2%
1231 | Muhlbach Eichstetten | 228 | Reinforcement of the existing 400kV OHL and deployment of a second 400kV circuit at existing dou-ble circuit OHL Muhlbach - Eichstetten, instead of the currently operated circuit Eichstetten - Vo-gelgrun (currently operated with 225kV). The project includes also a transformer in Sierentz substation to balance flows between 225kV and 400kV grid in the area. | 12-2026 | 2 | TRUE | Rescheduled | Adjustment of commissioning date to 2026 during the project planning process. | ACTransmissionLine | Muhlbach | Eichstetten | AC | None | 32 | 400 | 0 |  |  |  | 67.8 | 0 | 0.7 | 10%% | ++ | ++ | 0
353 | Krajnik-Baczyna | 230 | Construction of new 400 kV double circuit line Krajnik - Baczyna. | 03-2023 | 4 | FALSE | Rescheduled |  | ACTransmissionLine | Krajnik (PL) | Baczyna (PL) | AC | None | 70 | 400 | 0 |  |  |  | 38.54 | 0 | 0.116 | 5%% | ++ | ++ | 0 | 1 | BirdsDirective
355 | Mikulowa - Swiebodzice | 230 | Construction of new 400 kV double circuit line Mikulowa-Swiebodzice in place of existing 220 kV line together with expansion of 400/220/110kV Swiebodzice substation and 400/220/110kV Mikulowa substation. One circuit will be operating temporarily on 220 kV between stations Mikulowa and Swiebodzice with winter thermal limit 1290 A, summer thermal limit 990 A. | 12-2024 | 3 | FALSE | Rescheduled |  | ACTransmissionLine | Mikulowa (PL) | Swiebodzice (PL) | AC | None | 108 | 400 | 0 |  |  |  | 92.54 | 0 | 0.206 | 5%% | ++ | ++ | 0
1035 | Baczyna | 230 | Construction of new 400/110 kV Substation Baczyna to connect the new line Krajnik-Baczyna-Plewiska. | 12-2024 | 4 | FALSE | Delayed | The contract with the contractor was terminated in February 2020. The tender for a new contractor has already been concluded. | OnshoreSubstation | Baczyna | Baczyna | AC | None | 0 | 400 | 0 |  |  |  | 32.64 | 0 | 0.0675 | 5%%
1232 | Baczyna-Plewiska | 230 | Construction of new 400 kV double circuit line Baczyna - Plewiska with expansion of 400/220/110 kV Plewiska substation | 02-2023 | 4 | TRUE | Rescheduled |  | ACTransmissionLine | Baczyna | Plewiska | AC | None | 147 | 400 | 0 |  |  |  | 90.32 | 0 | 0.266 | 5%% | ++ | ++ | 0
1282 | 380 kV Grid Reinforcement Beznau - Tiengen | 231 | This projects helps to increase the cross border capacity between Switzerland and Germany by upgrading an existing line from 220 kV to 380 kV including internal reinforcements. | 12-2030 | 1 | TRUE | Investment on time |  | ACTransmissionLine | Beznau (CH) | Tiengen (DE) | AC | None | 11 | 380 | 0 | 2369 |  |  | 58 | 0 | 0.304 | 10%% | - | - | 0 | 0 | Other |  | 0 | Other
664 | HVDC LINE C - SUEDLINK | 235 | New DC-lines to integrate new wind generation from Northern Germany towards Southern Germany and Southern Europe for consumption and storage. | 12-2026 | 3 | TRUE | Investment on time |  | DCTransmissionLine | Brunsbüttel, Wilster | Großgartach, Bergrheinfeld West | DC | Bipolar | 700 | 525 | 4000 |  | VCS |  | 10500 | 0 | 84 | +-20%% | ++ | ++ | + (between sync areas) | 121 | OtherNatureProtectionAreasUnderNationalLaw |  | 157 | OtherNatureProtectionAreasUnderNationalLaw
1241 | Fenno-Skan 1 renewal | 239 | Replacement of the existing 400 kV HVDC cable interconnection between Finland and Sweden. Fennoskan 1 will be decommissioned and a new interconnector with the capacity of 800 MW will be built between FI and SE3, resulting in a total capacity of 1600 MW between FI and SE3. | 12-2040 | 1 | TRUE | Rescheduled | According to new studies, Fenno-Skan 1 lifetime can be continued until 2040 and this project will be commissioned after that. | OffshoreDCTransmissionCable | SE3 | FI | DC | None | 250 | 500 | 800 |  | VCS |  | 500 | 0 | 0.75 | +/- 20 %% | ++ | ++ | + (between sync areas)
1269 | New 400 kV overhead line Sombor (RS) - Ernestinovo (HR) | 243 | The project necessity stems for the need to increase the transfer capacity between RS and HR in order to accommodate connection of RES and improve market integration, according to the results based on TYNDP CBA. | 09-2035 | 1 | TRUE | Investment on time |  | ACTransmissionLine | SS Ernestinovo | SS Sombor 3 | AC | None | 70 | 400 | 0 | 1330 |  |  | 21.655 | 0 | 0.0245 | 15% | ++ | ++ | 0
1245 | Vigy - Uchtelfangen (or beyond) | 244 | Upgrade of existing transmission OHL between Vigy and Uchtelfangen (or beyond) to increase the thermal cross-border capacity. To reach a higher capacity the options are High Temperature Low Sag (HTLS) conductors or a reconstruction of the tie-line in the existing route . | 12-2029 | 2 | TRUE | Rescheduled | additionnal works in Ensdorf to receive the PST need to be coordinated with previous works in the same substation (upgrade transformer) for internal reason | ACTransmissionLine | Vigy (FR) | Uchtelfangen (DE) | AC | None | 65 | 400 | 0 |  |  |  | 78 | 0 | 0.624 | 10%% | - | - | 0
1514 | Power flow control between Vigy and Ensdorf | 244 | Installation of Phase Shift Transformers (PSTs) in Ensdorf substation to allow an optimal use of the capacity increase. | 12-2029 | 2 | FALSE | Rescheduled |  | PhaseShiftingTransformer | Vigy (FR) | Ensdorf (DE) | AC | None | 0 | 400 | 0 |  |  |  | 55 | 0 | 0.44 | 10%%
1381 | AQUIND Interconnector | 247 | AQUIND Interconnector is a proposed High Voltage Direct Current (HVDC) subsea and underground electric power transmission link between Great Britain (Lovedean substation, Hampshire) and France (Barnabos substation, Seine-Maritime) with a net transmission capacity of 2,000 MW. The Interconnector is designed as two parallel monopole 1000 MW circuits employing Voltage Source Converter technology. | 09-2026 | 3 | TRUE | Delayed | Since TYNDP 2020, the situation with COVID and ongoing negotiations on Brexit and the Trade and Cooperation Agreement resulted in a delay with permitting and regulatory procedures in GB and France. Respectively commissioning of the project moved to 2026. | OffshoreDCTransmissionCable | Lovedean (GB) | Barnabos (FR) | DC | Monopolar | 240 | 320 | 2075 |  | VCS |  | 1400 | 36 | 14 | +/-10% | ++ | ++ | + (between sync areas)
1384 | Merchant line "Castasegna (CH) - Mese (IT)" | 250 | The planned Transmission project is a merchant line on the swiss-italian border between Castasegna (CH) and Mese (IT). The planned Cable connection in 220 kV AC has a length of around 14 km, 13.5 of witch in Italy. In connection with the realisation of the project a Rationalisation of the 380 and 132 kV Grid in the region Mese (Provincia di Sondrio) is planned. The expected NTC increase is around 200 MW.The main Project elements are (merchant line): 220 kV Connection to the Swiss HVG in Castasegna; 220 kV Cable line of around 14 km between Castasegna and Mese; 220/380 kV Substation with PST 250 MVA in Mese. The Grid Rationalisation in the Region of Mese foresees the following actions: Displacement of 2 km of the 380 kV Line "Soazza - Bulciago"; "Realisation of a new 380/132 kV Substation in Mese (Transformation 2 x 250 MVA); Displacement of 0.8 km of 132 kV Lines; Realisation of 2.6 km of 132 kV Cable connections; Demolition of 2.45 km of 380 kV line and 2.3 km of 132 kV lines." | 03-2025 | 3 | TRUE | Delayed | The permitting phase in Italy is ongoing since April 2014 but we are still facing some challenges regarding Environmental impact of the 380/132kV Substation Terna in Mese. Commissioning expected in 2025. | ACTransmissionLine | Castasegna | Mese | AC | None | 14 | 220 | 0 | 250 |  |  | 90 | 0 | 0.1 | +/-15% | [9 empty] | Environmental positive impact due to the connected grid rationalisation 380/132kV in the region of Mese. Improvement N-1 security for hydro power plant production transmission in Castasegna (CH).
1050 | Van Eyck - Gramme: HTLS upgrade | 252 | Upgrade of this double-circuit axis to HTLS conductors. Note that recently installed conductors along this axis anticipated the future HTLS upgrade, they don't have to be further upgraded. | 12-2029 | 2 | FALSE | Investment on time |  | ACTransmissionLine | Van Eyck | Gramme | AC | None | 90 | 380 | 0 | 3000 |  |  | 140 | 0 | 0.4 | 25%% | - | - | 0
1515 | Gramme - Courcelles: HTLS upgrade | 252 | Upgrade of this double-circuit axis to HTLS conductors | 12-2038 | 2 | FALSE | Rescheduled |  | ACTransmissionLine | Gramme | Courcelles | AC | None | 60 | 380 | 0 | 3000 |  |  | 150 | 0 | 0.3 | 25%% | - | - | 0
1516 | Bruegel - Courcelles: HTLS upgrade | 252 | Upgrade of this double-circuit axis to HTLS conductors | 12-2035 | 2 | FALSE | Investment on time |  | ACTransmissionLine | Bruegel | Courcelles | AC | None | 47 | 380 | 0 | 3000 |  |  | 110 | 0 | 0.2 | 25%% | - | - | 0
1517 | Mercator - Bruegel: HTLS upgrade | 252 | Upgrade of this double-circuit axis to HTLS conductors | 12-2026 | 3 | TRUE | Delayed |  | ACTransmissionLine | Mercator | Bruegel | AC | None | 16 | 380 | 0 | 3000 |  |  | 80 | 0 | 0.1 | 25%% | - | - | 0 | 1.5 1.5 | HabitatsDirective BirdsDirective |  | 15 | HabitatsDirective
1676 | Mercator - Massenhoven: HTLS upgrade | 252 | Upgrade of this double-circuit axis to HTLS conductors | 12-2030 | 2 | FALSE | Investment on time |  | ACTransmissionLine | Mercator | Massenhoven | AC | None | 36 | 380 | 0 | 3000 |  |  | 140 | 0 | 0.2 | 25% | - | - | 0
1225 | PST in Cornier | 253 | Phase Shifter Transformer in order to attract the flows and alleviate the congestion on the France-switzerland interconnection west of Lake Geneva. | 12-2031 | 1 | TRUE | Investment on time |  | PhaseShiftingTransformer | Cornier (FR) | Cornier (FR) | AC | None | 0 | 400 | 0 |  |  |  | 15 | 0 | 0.1 | 10%% |  |  |  | 0 | None |  | 0 | None
660 | HVDC Line A South - Ultranet | 254 | New HVDC-lines from Osterath to Philippsburg to integrate new wind generation especially from North Sea towards Central-South Germany for consumption and storage. | 12-2026 | 3 | TRUE | Rescheduled | Adjustment of commissioning date to 2026 due to the long and complex approval process. | DCTransmissionLine | Osterath (DE) | Philippsburg (DE) | DC | Bipolar | 343 | 400 | 2000 |  | VCS |  | 1540 | 0 | 12.3 | 10%% |  |  |  | 12.6 16.7 209 | HabitatsDirective BirdsDirective OtherNatureProtectionAreasUnderNationalLaw |  | 4.5 15.4 183.3 49.5 | HabitatsDirective RAMSARSite IUCNKeyBiodiversityAreas MarinStrategyFrameworkDirective
1205 | HU-RO | 259 | New 120 km single circuit 400 kV OHL between Hungary and Romania (90 km on Hungarian and 30 km on Romanian side). Internal investments in Romania associated to the project are also included. | 12-2030 | 2 | TRUE | Investment on time |  | ACTransmissionLine | Józsa | Oradea | AC | None | 120 | 400 | 0 | 1384 |  |  | 110 | 2.88 | 1.1 | -5%, +5%% | ++ | ++ | 0
1832 | RO1 | 259 | New 400/220 kV transformer in substation Rosiori | 12-2027 | 2 | FALSE | Investment on time |  | Transformer | Rosiori (RO) | Rosiori (RO) | AC | None | 0 | 0 | 0 | 400 |  |  | 5.18 | 0.405 | 0.052 | ± 5%%
1833 | RO2 | 259 | Reconductoring 220 kV OH line Urechesti-Tg. Jiu | 12-2028 | 2 | FALSE | Investment on time |  | ACTransmissionLine | Urechesti (RO) | Targu Jiu (RO) | AC | None | 18 | 400 | 0 | 576.15 |  |  | 1.38 | 0.108 | 0.014 | ±5%%
1834 | RO3 | 259 | Reconductoring 220 kV OH line Tg. Jiu-Paroseni | 12-2028 | 2 | FALSE | Investment on time |  | ACTransmissionLine | Targu Jiu (RO) | Paroseni (RO) | AC | None | 38 | 400 | 0 | 576.15 |  |  | 2.91 | 0.228 | 0.029 | ± 5%%
1835 | RO4 | 259 | Reconductoring 220 kV OH line Paroseni- Baru Mare | 12-2028 | 2 | FALSE | Investment on time |  | ACTransmissionLine | Paroseni (RO) | Baru Mare (RO) | AC | None | 20 | 400 | 0 | 576.15 |  |  | 1.53 | 0.12 | 0.015 | ± 5%%
1836 | RO5 | 259 | Reconductoring 220 kV OH line Baru Mare-Hasdat | 12-2028 | 2 | FALSE | Investment on time |  | ACTransmissionLine | Baru Mare (RO) | Hasdat (RO) | AC | None | 44 | 400 | 0 | 626.55 |  |  | 3.37 | 0.264 | 0.034 | ±5%%
1255 | Interconnector GB-NL | 260 | Multi-purpose interconnector between GB and NL also connecting GB and NL windfarms. | 12-2030 | 1 | TRUE | Investment on time |  | OffshoreDCTransmissionCable | TBD | TBD | DC | None | 0 | 525 | 1800 |  | VCS |  | 850 | 0 | 6 | ±10%% | ++ | ++ | + (between sync areas)
1258 | Rüthi - Bonaduz/Mettlen | 263 | Integration of the new 380 kV tie-line Rüthi (CH) - Meiningen (AT) through optimisations between Rüthi and Mettlen, Rüthi and Bonaduz and the construction of a new 380 kV substation and a new 380/220 kV transformer in Rüthi. | 12-2035 | 1 | FALSE | Investment on time |  | ACTransmissionLine | Rüthi | Mettlen & Bonaduz | AC | None | 1 | 380 | 0 |  |  |  | 68.89 | 0 | 0.34 | 10%% | ++ | ++ | 0 | 0 | Other None |  | 0 | Other
1476 | Wullenstetten - Border Area (DE-AT) | 263 | Between point Wullenstetten and point Niederwangen an upgrade of an existing 380-kV-line is necessary. Furthermore, between switching point Neuravensburg and Austrian National border (AT) a new line with a significantly higher transmission capacity will be constructed in an existing corridor. | 12-2030 | 2 | TRUE | Rescheduled | Scope of the project changed due to technical reasons. Investment 1476 Wullenstetten – National Border DE-AT was previously under Project 322. | ACTransmissionLine | Wullenstetten (DE) | Austrian National border (AT) | AC | None | 95 | 380 | 0 | 2369 |  |  | 98.3 | 0 | 0.8 | 10%% | - | - | 0
1583 | Vorarlberg | 263 | Voltage increase of all existing lines to 380 kV (without an increase of the line cross-section) and 2 new 380/220 kV transformers in Bürs | 12-2035 | 1 | TRUE | Investment on time |  | ACTransmissionLine | Rüthi | Border area (DE-AT) | AC | None | 1 | 380 | 0 |  |  |  | 300 | 0 | 1.5 | 10%% | ++ | ++ | 0 | 0 | Other |  | 0 | Other
1262 | Hansa PowerBridge II | 267 | Possible second HVDC cable interconnector between southern Sweden (Bidding area SE4) and Germany (50Hertz). This project candidate is driven by market based target capacities found in the Common Planning Studies by Regional Group Baltic Sea. | 12-2035 | 1 | TRUE | Delayed | Postponement of commissioning, currently the full focus is on HBPI | OffshoreDCTransmissionCable | Hurva (SE4) | Sanitz/Dettmannsdorf (DE) | DC | None | 300 | 300 | 700 |  | VCS |  | 600 | 0 | 1 | +-10%% | ++ | ++ | + (between sync areas)
1211 | HVDC Aragon region -Marsillon | 270 | New axis Aragon region -Marsillon | 09-2030 | 2 | TRUE | Investment on time |  | DCTransmissionLine | Aragon region | Marsillon | DC | None | 120 | 320 | 2000 |  | VCS |  | 1149 | 0 | 3.26 | 10%% | ++ | ++ | + (between sync areas) | 61 | Other |  | 12 | HabitatsDirective
1212 | New axis Ejea-Aragon region 400 kV | 270 | New AC line (double circuit 400kV) between Ejea and Aragon region where the converter station is located | 09-2030 | 2 | FALSE | Investment on time |  | ACTransmissionLine | Ejea de los Caballeros | Aragon region | AC | None | 110 | 400 | 0 |  |  |  | 62 | 0 | 2.72 | 10%% | ++ | ++ | 0
1214 | Ejea de los Caballeros subestation | 270 | New 400kV Ejea de los Caballeros subestation and connection to the lines La Serna-Magallon and Magallon Peñalba | 09-2030 | 2 | FALSE | Investment on time |  | OnshoreSubstation | Ejea de los Caballeros | Ejea de los Caballeros | AC | None | 0 | 400 | 0 |  |  |  | 0 | 0 | 0.02 | 10%%
1215 | Aragon region subestation | 270 | New 400 kV Aragon region subestation and connection to existing network and future cross border project | 09-2030 | 2 | FALSE | Investment on time |  | OnshoreSubstation | Aragon region | Aragon region | AC | None | 0 | 400 | 0 |  | VCS |  | 10 | 0 | 0.03 | 10%%
1206 | HVDC Pamplona area - Cantegrit | 276 | HVDC Pamplona area(Spain) -Cantegrit (France) | 12-2030 | 2 | TRUE | Investment on time |  | DCTransmissionLine | Pamplona area | Cantegrit | DC | None | 225 | 320 | 2000 |  | VCS |  | 1245 | 0 | 5.33 | 10%% | ++ | ++ | + (between sync areas) | 20 | Other |  | 2 | HabitatsDirective
1207 | Upgrade Cantegrit-Saucats | 276 | Upgrade of 2* 400 kV lines Cantegrit-Saucats | 12-2030 | 2 | FALSE | Rescheduled |  | ACTransmissionLine | Cantegrit | Saucats | AC | None | 70 | 400 | 0 |  |  |  | 150 | 0 | 2 | 10%% | - | - | 0
1208 | Upgrade Cantegrit-Marsillon | 276 | Upgrade of existing 2*225kV line Cantegrit-Marsillon to 1* 400kV | 12-2030 | 2 | FALSE | Rescheduled |  | ACTransmissionLine | Cantegrit | Marsillon | AC | None | 80 | 400 | 0 |  |  |  | 150 | 0 | 2 | 10%%
1210 | New substation Pamplona area | 276 | New substation Pamplona area 400 kV and connection to the 400 kV line Ichaso-Castejón/Muruarte? | 12-2030 | 2 | FALSE | Investment on time |  | OnshoreSubstation | Pamplona area | Pamplona area | AC | None | 0 | 400 | 0 |  |  |  | 9 | 0 | 0.17 | 10%%
1008 | Study Lonny-Achene-Gramme | 280 | Installation of PST(s) and/or line capacity upgrade of Lonny-Achene-Gramme | 12-2030 | 1 | TRUE | Investment on time |  | ACTransmissionLine | Lonny (FR) | Gramme (BE) | AC | None | 100 | 400 | 0 | 2700 |  |  | 105 | 0 | 0.1 | 25%% | - | - | 0
1378 | TuNur DC | 283 | The HVDC transmission architecture is based on two independent bipolar +/-525 kV systems of 1GW. The HVDC converter is based on VSC (Voltage Source Converter) technology, providing high reliability and efficiency of the transmission system. TuNur DC will consist of two independent bipolar +/-525 kV systems of 1GW. Each bipolar system will consist of a DC overhead line in Tunisia spanning from the power plant to the shoring point, submarine cable from the Tunisian Northern coast to Montalto di Castro, and VSC HVDC converter stations at both terminal points. | 12-2028 | 1 | TRUE | Delayed | The Tunisian regulatory framework has been settled only recently and this delayed the overall permitting process. | OffshoreDCTransmissionCable | Rejim Maatoug (TUN) VSC HVDC - +/- 500 kV DC – 2x 1GW | Montalto di Castro (ITA) VSC HVDC - +/- 500 kV DC - 400 kV AC– 2x 1GW | DC | Bipolar | 1308 | 525 | 2000 |  | VCS |  | 2696 | 671 | 41 | 8% | ++ | ++ | + (between sync areas) | 1 | RAMSARSite |  |  |  |  | TuNur DC: Job Creation - Creation of numerous qualified jobs in Tunisia for the construction and O&M of the land lines and HVDC converters
1430 | TuNur AC | 283 | 400 kV AC underground cables from the HVDC converter in Montalto to Terna’s 400 kV station in Montalto. CAPEX includes 2 circuit breaker bays within Terna’s station. | 09-2028 | 1 | FALSE | Delayed | The Tunisian regulatory framework has been settled only recently and this delayed the overall permitting process. | ACTransmissionLine | Montalto di Castro (ITA) VSC HVDC - +/- 500 kV DC - 400 kV AC – 2x 1GW | Montalto di Castro (IT) Terna station 400 kV AC | AC | None | 2 | 400 | 0 |  |  |  | 16 | 1 | 0.04 | 8% of the overall project cost as exact length is not yet confirmed, it being understood that the impact of the short AC cable on the overall project will be negligible.% | ++ | ++ | 0 | [6 empty] | TuNur DC: Job Creation - Creation of numerous qualified jobs in Tunisia for the construction and O&M of the land lines and HVDC converters
1383 | GridLink | 285 | UK-France, 1.4GW HVDC Interconnector | 12-2025 | 3 | TRUE | Delayed | Brexit - investment request submitted but declared void on 24 December 2020 as there were no provisions in the FTA which would allow the French & UK regulators to continue to have competence to decide the investment request. A new investment request was submitted solely to CRE in March 2021. | OffshoreDCTransmissionCable | Kingsnorth (UK) | Warande (Gravelines, France) | DC | Monopolar | 158 | 525 | 1400 |  | VCS |  | 885 | 885 | 23.8 | 10%
1385 | Greenlink | 286 | A subsea HVDC interconnector between Wales and Ireland | 11-2024 | 4 | TRUE | Rescheduled | The PCI was rescheduled due 2 main reasons. 1) Regulatory processes in the Republic of Ireland has taken longer than anticipated. 2) Irish planning process has taken longer than planned. The project has now received approvals from regulators from both UK and Ireland and its planning permission. The project expects financial close in December 21 | OffshoreDCTransmissionCable | Great Island | Pembroke | DC | Monopolar | 200 | 320 | 504 |  | VCS |  | 500 | 0 | 14 | +/-5%% | ++ | ++ | + (between sync areas) | 0.08 7.8 49.6 0.7 0.4 22.3 36.9 0.7 3.2 | HabitatsDirective HabitatsDirective HabitatsDirective HabitatsDirective HabitatsDirective HabitatsDirective HabitatsDirective OtherNatureProtectionAreasUnderNationalLaw OtherNatureProtectionAreasUnderNationalLaw |  |  |  |  | Greenlink is in the construction stage. Greenlink completed an Environmental Impact Assessment as part of the development process which was submitted as part of the planning application to the relevant permitting and competent authorities for review. Following review the relevant permitting and competent authorities have issued the permits required to construct Greenlink. If you require further information on the documentation submitted for Onshore Ireland, Onshore Wales and Offshore across the Project please get in touch.
1431 | Lavrio - Levitha | 293 | New DC link (2 converter SS + 245 km DC subm. cable) to connect 582MW of offshore WF generation to the mainland (Area of Athens) | 01-2025 | 1 | TRUE | Investment on time |  | OffshoreDCTransmissionCable | Lavrio | Levitha | DC | Bipolar | 245 | 320 | 600 |  | VCS |  | 520 | 2 | 5 | 8%% | ++ | ++ | + (between sync areas)
1432 | Levitha - Crete | 293 | Interconnection of the Crete Island to the Greek Mainland via Levitha converter station. | 01-2026 | 1 | FALSE | Investment on time |  | OffshoreDCTransmissionCable | Levitha | Atherinolakkos Crete | DC | Bipolar | 250 | 320 | 600 |  | VCS |  | 530 | 2 | 5.5 | 8%% | ++ | ++ | + (between sync areas)
1433 | Levitha - Syrna | 293 | Connection Wind Farms with AC Substations at Levitha and Syrna | 02-2025 | 1 | FALSE | Investment on time |  | OffshoreACTransmissionCable | Levitha | Syrna | AC | None | 81 | 220 | 0 | 320 |  |  | 150 | 1 | 3 | 5%% | ++ | ++ | 0
1434 | Kinaros - Levitha | 293 | AC Submarine cable to connect Kinaros substation to the AC side of Levitha Substation | 12-2024 | 1 | FALSE | Investment on time |  | OffshoreACTransmissionCable | Kinaros | Levitha | AC | None | 15 | 220 | 0 | 100 |  |  | 15 | 0 | 1 | 5%% | ++ | ++ | 0
1704 | Levitha - Kos | 293 | HVAC Submarine cable connecting Levitha offshore Wind Farm HV substation to Dodecanese (Kos & Rhodes HV Substation) | 03-2026 | 1 | FALSE | New Investment |  | OffshoreACTransmissionCable | Levitha | Kos | AC | None | 60 | 220 | 0 | 200 |  |  | 120 | 0.5 | 2.5 | 5%% | ++ | ++ | 0
445 | BRABO II: Zandvliet - Lillo - Liefkenshoek | 297 | The second phase of the BRABO project consists of the construction of a new double circuit 380kV overhead line from Zandvliet via Lillo to Liefkenshoek where the new line will be the temporarily connected to the existing 380kV line Doel-Mercator.This new line will be constructed making use of the corridor of the existing 150kV overhead line Zandvliet-Oorderen-Lillo, which will be undergrounded. | 01-2021 | 5 | TRUE | Investment on time |  | ACTransmissionLine | Zandvliet | Lillo - Liefkenshoek | AC | None | 18 | 380 | 0 | 1900 |  |  | 100 | 0 | 0.1 | 5%% | ++ | ++ | 0 | 1.5 1 | HabitatsDirective BirdsDirective
604 | BRABO III: Liefkenshoek - Mercator | 297 | The existing 150kV overhead will be upgraded to a single 380kV overhead line between the site Liefkenshoek and the substation Mercator. To facilitate this upgrade, the adjacent 150kV grid will be adapted. | 07-2025 | 4 | FALSE | Investment on time |  | ACTransmissionLine | Liefkenshoek (BE) | Mercator (BE) | AC | None | 19 | 380 | 0 | 1900 |  |  | 70 | 0 | 0.1 | 25%% | ++ | ++ | 0 | 4 | BirdsDirective |  | 14.7 | HabitatsDirective
605 | BRABO II: Lillo 380 | 297 | "This concerns the construction of the 380kV substation Lillo, including a 380/150 kV transformer, as part of the second phase of the BRABO-project." | 01-2020 | 5 | FALSE | Investment on time |  | OnshoreSubstation | Lillo (BE) | Lillo (BE) | AC | None | 0 | 380 | 0 |  |  |  | 15 | 0 | 0.1 | 5%% | ++ | ++ | 0 |  |  |  | 15.5 | HabitatsDirective
1458 | SACOI3 | 299 | New HVDC triterminal link between Italy mainland, Corsica and Sardinia replacing existing link SACOI2 | 12-2027 | 3 | TRUE | Delayed | Delayed due to permitting reasons. | DCTransmissionLine | Codrongianos - Lucciana | Suvereto | DC | Bipolar | 300 | 200 | 400 |  | VCS |  | 1300 | 0 | 7.2 | 10% | ++ | ++ | + (between sync areas) | 0 | Other | - | 3 | Other | -
1628 | NeuConnect Interconnector | 309 | 1.4GW HVDC Interconnector between UK and Germany | 06-2026 | 3 | TRUE | Delayed | The project connection date is delayed due events outwith of NeuConnect's direct control | OffshoreDCTransmissionCable | Grain West 400kV Substation | Fedderwarden 380kV Substation | DC | Bipolar | 720 | 500 | 1400 |  | VCS |  | 2075.82 | 49 | 32.3 | 10%%
1472 | St. Peter (AT) - Tauern (AT) | 312 | new 380-kV-Line | 12-2025 | 4 | TRUE | Delayed | Duration of permitting process. | ACTransmissionLine | St. Peter | Tauern | AC | None | 128 | 380 | 0 |  |  |  | 890 | 0 | 2.67 | 10%% | [6 empty] | 43 | None
1473 | Isar/Altheim/Ottenhofen - St. Peter | 313 | New 380kV double circuit OHL Isar/Altheim/Ottenhofen - St. Peter including new 380kV switchgears Altheim, Pirach, Simbach and St. Peter. | 12-2026 | 3 | TRUE | Delayed | Delay due to complex and long permitting process | ACTransmissionLine | Isar/Altheim/Ottenhofen (DE) | St. Peter (AT) | AC | None | 90 | 380 | 0 |  |  |  | 484.6 | 0 | 3.4 | 10% |  |  |  | 4 | OtherNatureProtectionAreasUnderNationalLaw
1478 | Dekani (SI) - Zaule (IT) interconnection | 323 | The Zaule (IT) - Dekani (SI) interconnection is a third party cross-border electrical line promoted by Adria Link Srl, E3 d.o.o. and HSE d.o.o.. The project concerns an underground cable 110kV a.c. merchant line, 150 MW from Zaule (IT) substation to Dekani substation, including a 110/135 kV Phase Shifter Transformer. | 04-2025 | 3 | TRUE | Delayed | The promoters asked to the respective NRA for the NTC recalculation not subject to conditions (EG. third party network reinforcements), which will be guaranteed for the exemption period and from the entry into the new commercial operation date (COD) of the interconnector. The process is still ongoing. | ACTransmissionLine | DEKANI | ZAULE | AC | None | 11 | 110 | 0 | 125 |  |  | 16.6 | 0.36 | 0.3 | 7%% | ++ | ++ | 0
1482 | Redipuglia (IT) - Vrtojba (SI) Interconnection | 324 | "The Redipuglia (IT) - Vrtojba (SI) interconnection is a third party cross-border electrical line promoted by Adria Link Srl, E3 d.o.o. and HSE d.o.o.. The project concerns an underground cable 110kV a.c. merchant line, 150 MW from Redipuglia (IT) substation to Vrtojba (SI) substation, including a 110/135 kV Phase Shifter Transformer." | 06-2024 | 3 | TRUE | Delayed | The promoter asked the respective NRA for the NTC recalculation not subject to conditions (eg third party network reinforcements), which will be guaranteed for the exemption period and from the entry into the new commercial operation date (COD) of the interconnector. The process is still ongoing. | ACTransmissionLine | REDIPUGLIA | VRTOJBA | AC | None | 22.5 | 110 | 0 | 125 |  |  | 26 | 0.54 | 0.4 | 7%% | ++ | ++ | 0
1483 | Upgrade Obersielach (AT) - Podlog (SI) | 325 | upgrade from 220 kV to 380 kV | 06-2034 | 1 | TRUE | Investment on time |  | ACTransmissionLine | Obersielach (AT) | Podlog (SI) | AC | None | 70 | 380 | 0 |  |  |  | 210 | 0 | 0.5 | 10% | ++ | ++ | 0 | 4 | OtherNatureProtectionAreasUnderNationalLaw |  | 81 | OtherNatureProtectionAreasUnderNationalLaw
1620 | Substation Aach | 328 | New 400/220-kV-substation | 12-2026 | 2 | FALSE | Investment on time |  | OnshoreSubstation | N/A | N/A | AC | None | 0 | 400 | 0 |  |  |  | 40 | 0 | 0.32 | 10%% | [9 empty] | The project replaces an existing overhead line.
1629 | Substation Bofferdange | 328 | New 400/220/110 kV substation including transformer 400/220 kV to be commissioned in Bofferdange (LU) | 12-2026 | 3 | FALSE | Investment on time |  | OnshoreSubstation | N/A | N/A | AC | None | 0 | 400 | 0 |  |  |  | 42 | 0 | 0.34 | 10%% | [9 empty] | The project replaces an existing overhead line.
1630 | AC Overhead Line Aach-Bofferdange | 328 | New AC Overhead Line between Germany and Luxembourg | 12-2026 | 3 | TRUE | Investment on time |  | ACTransmissionLine | Aach (DE) | Bofferdange (LU) | AC | None | 40 | 400 | 0 |  |  |  | 83.5 | 0 | 0.67 | 10%% | ++ | ++ | 0 | [6 empty] | The project replaces an existing overhead line.
1518 | Stevin-Izegem/Avelgem: new corridor | 329 | Realisation of a new AC corridor up to 6 GW capacity | 12-2028 | 3 | TRUE | Investment on time |  | ACTransmissionLine | Stevin | Courcelles | AC | None | 90 | 380 | 0 | 3000 |  |  | 400 | 0 | 0.3 | 25%% | ++ | ++ | 0
1498 | New CZ-SK 400 kV interconnector | 330 | This investment consists of single circuit 400 kV OHL Otrokovice (CZ) - Ladce (SK). | 12-2035 | 1 | TRUE | New Investment |  | ACTransmissionLine | Otrokovice (CZ) | Ladce (SK) | AC | None | 78 | 400 | 0 | 1694 |  |  | 83.2 | 0 | 0.37 | ±10%%
1499 | New 400 kV substation Ladce | 330 | This investment consists of the new 400 kV substation Ladce, which will replace existing 220 kV substation Považská Bystrica and will therefore increase security of supply in this particular region. After commissioning this new 400 kV substation it will be possible to build new 400 kV cross-border OHL from Ladce (SK) to Otrokovice (CZ). | 12-2026 | 2 | FALSE | New Investment |  | OnshoreSubstation | Ladce (SK) | Ladce (SK) | AC | None | 0 | 400 | 0 |  |  |  | 3.1 | 0 | 0.25 | ±10%%
1496 | PST Foretaille | 333 | Installation of two PSTs in Foretaille that control the flow on the Foretaille - Verbois 220 kV double line | 12-2031 | 1 | TRUE | Investment on time |  | PhaseShiftingTransformer | Foretaille | Foretaille | AC | None | 0 | 220 | 0 | 1200 |  |  | 35 | 0 | 0.18 | 10%% | + | + | 0 | 0 | Other |  | 0 | Other
1504 | Danish Hub | 335 | Hub installation suitable to connect 2GW of HVDC systems to Danish shore and up to 4GW of nearby offshore wind. Danish hub is connected to German and Dutch hub with 2 GW HVDC systems each. | 01-2032 | 1 | TRUE | Investment on time |  | OffshoreSubstation | 0 | 0 | AC | None | 0 | 0 | 0 |  |  |  | 1994 | 0 | 6.6 | The Capex uncertainty range for this asset is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this.%
1505 | Interconnection DKw to Danish hub | 335 | HVDC connector including substations interfacing the Danish hub and the Western Danish power system. | 01-2032 | 1 | FALSE | Investment on time |  | OffshoreDCTransmissionCable | REVSING | Danish hub | DC | None | 256 | 525 | 2000 |  | VCS |  | 1160 | 0 | 5.8 | The Capex uncertainty range for this 525kV link covers -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this.%
1506 | Interconnection NL Maasvlakte to Dutch hub (#1) | 335 | One of two HVDC connectors including substations interfacing the Dutch hub and the Dutch power system. | 01-2035 | 1 | FALSE | Investment on time |  | OffshoreDCTransmissionCable | Maasvlakte 380 kV | Dutch hub | DC | None | 356 | 525 | 2000 |  | VCS |  | 1710 | 0 | 8.6 | The Capex uncertainty range for this 525kV link is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this.%
1507 | Interconnection NL Maasvlakte to Dutch hub (#2) | 335 | One of two HVDC connectors including substations interfacing the Dutch hub and the Dutch power system. | 01-2035 | 1 | FALSE | Investment on time |  | OffshoreDCTransmissionCable | Maasvlakte 380 kV | Dutch hub | DC | None | 356 | 525 | 2000 |  | VCS |  | 1710 | 0 | 8.6 | The Capex uncertainty range for this 525kV link is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this.%
1508 | Interconnection DE (Heide(West)) to German hub | 335 | One of three HVDC connectors including substations interfacing the German hub and the German power system. | 01-2035 | 1 | FALSE | Investment on time |  | OffshoreDCTransmissionCable | Heide(West) | German hub | DC | None | 348 | 525 | 2000 |  | VCS |  | 1681 | 0 | 8.4 | The Capex uncertainty range for this 525kV link is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this.%
1509 | Interconnection DE (area north of Bremen) to German hub | 335 | One of three HVDC connectors including substations interfacing the German hub and the German power system. | 01-2035 | 1 | FALSE | Investment on time |  | OffshoreDCTransmissionCable | German substation located in the area north of Bremen | German hub | DC | None | 423 | 525 | 2000 |  | VCS |  | 1960 | 0 | 9.8 | The Capex uncertainty range for this 525kV link is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this.%
1511 | Interconnection DE (area of Rastede) to German hub | 335 | One of three HVDC connectors including substations interfacing the German hub and the German power system. | 01-2035 | 1 | FALSE | Investment on time |  | OffshoreDCTransmissionCable | German substation located in the area of Rastede | German hub | DC | None | 369 | 525 | 2000 |  | VCS |  | 1759 | 0 | 8.8 | The Capex uncertainty range for this 525kV link is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this.%
1815 | Dutch Hub | 335 | Hub installation suitable to connect 4GW of HVDC systems to Dutch shore and up to 4W of nearby offshore wind. Dutch hub is connected to the Danish and German hub with 2 GW HVDC systems each. | 01-2035 | 1 | TRUE | Investment on time |  | OffshoreSubstation | 0 | 0 | AC | None | 0 | 0 | 0 |  |  |  | 1994 | 0 | 6.6 | The Capex uncertainty range for this asset is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this.%
1816 | German Hub | 335 | Hub installation suitable to connect 6 GW of HVDC systems to German shore and up to 6 GW of nearby offshore wind. German hub is connected to the Danish and Dutch hub with 2 GW HVDC systems each. | 01-2035 | 1 | TRUE | Investment on time |  | OffshoreSubstation | 0 | 0 | AC | None | 0 | 0 | 0 |  |  |  | 2991 | 0 | 10 | The Capex uncertainty range for this asset is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this.%
1817 | Interconnection Danish hub to Dutch hub | 335 | One of three HVDC connectors including substations interfacing 2 of the 3 hubs | 01-2035 | 1 | FALSE | Investment on time |  | OffshoreDCTransmissionCable | Danish hub | Dutch hub | DC | None | 351 | 525 | 2000 |  | VCS |  | 1306 | 0 | 6.5 | The Capex uncertainty range for this 525kV link is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this.%
1818 | Interconnection Danish hub to German hub | 335 | One of three HVDC connectors including substations interfacing 2 of the 3 hubs | 01-2035 | 1 | FALSE | Investment on time |  | OffshoreDCTransmissionCable | Danish hub | German hub | DC | None | 226 | 525 | 2000 |  | VCS |  | 841 | 0 | 4.2 | The Capex uncertainty range for this 525kV link is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this.%
1819 | Interconnection Dutch hub to German hub | 335 | One of three HVDC connectors including substations interfacing 2 of the 3 hubs | 01-2035 | 1 | FALSE | Investment on time |  | OffshoreDCTransmissionCable | Dutch hub | German hub | DC | None | 125 | 525 | 2000 |  | VCS |  | 465 | 0 | 2.3 | The Capex uncertainty range for this 525kV link is -20% to +30%. This can be explained by the different costs which are registered for currently realized projects to connect offshore windfarms. This range can be explained by the project specific differences. Since there is no clarity on the project specifics in this phase of the project, the uncertainty range thereby reflects this.%
1521 | New HVDC line between Villanova and Fano existing 400 kV substations | 338 | The project envisages a new HVDC interconnection between the Centro Sud (SE Villanova) and Centro Nord (SE Fano) market sections with a capacity increase of 1000 MW. In addition, the interconnection will bring further benefits to the electricity system, including improving the dynamic stability of the grid and the system's response to possible disturbances. | 12-2028 | 2 | TRUE | New Investment |  | OffshoreDCTransmissionCable | Villanova | Fano | DC | None | 560 | 500 | 1000 |  | VCS |  | 1310 | 0 | 3.03 | 10% | ++ | ++ | + (between sync areas)
1557 | Tyrrhenian HVDC link - West | 339 | The project foresees a new HVDC interconnection between Sardinia (SE Selargius) and Sicily (SE Caracoli). The design solution envisages a two-terminal plant configuration as it will allow greater reliability to the link by increasing the security and stability of the two islands, as well as an increase in NTC between the two market areas of 1000 MW. | 12-2027 | 3 | TRUE | Investment on time |  | OffshoreDCTransmissionCable | Caracoli | Selargius | DC | None | 900 | 500 | 1000 |  | VCS |  | 1900 | 0 | 3.6 | 10% | ++ | ++ | + (between sync areas) | 43 | Other | - | 36 | Other | -
1795 | Tyrrhenian HVDC link - East | 339 | The project envisages a new HVDC interconnection between Campania (SE Montecorvino) and Sicily (SE Caracoli). The design solution envisages a bi-terminal plant configuration as it allows for greater reliability of the connection by increasing the safety and stability of the connection between Sicily and the continent as well as an increase of NTC between the two market areas equal to 1000 MW. | 12-2028 | 3 | FALSE | New Investment | - | OffshoreDCTransmissionCable | Montecorvino | Caracoli | DC | None | 424 | 500 | 1000 |  | VCS |  | 1800 | 0 | 3.4 | 0%
1519 | Avelgem-Courcelles | 340 | Realisation of a 6 GW new corridor including PSTs | 12-2029 | 3 | TRUE | Investment on time |  | ACTransmissionLine | Avelgem | Courcelles | AC | None | 100 | 380 | 0 | 3000 |  |  | 500 | 0 | 0.5 | 25%% | ++ | ++ | 0
1536 | Portile de Fier (RO) - Djerdap (RS) 2nd | 341 | Portile de Fier (RO) - Djerdap (RS) 2nd . Doubling the existing OHL 400 kV (1.5 km on Serbian (thermal limit 1800 A) and 0.5 km on Romanian( thermal limit 2192 A) Side) | 09-2029 | 2 | TRUE | Ahead of time |  | ACTransmissionLine | Portile de Fier | Djerdap | AC | None | 2 | 400 | 0 | 1247 |  |  | 4 | 0.01 | 0.04 | 5% | ++ | ++ | 0
1537 | New SS 400/110 kV Belgrade 50 | 341 | New SS 400/110 kV Belgrade 50 (former name Belgrade West) | 09-2028 | 2 | FALSE | Ahead of time |  | Transformer | Belgrade 50 | Belgrade 50 | AC | None | 0 | 400 | 0 | 600 |  |  | 45 | 0 | 0.45 | 5%
1538 | New OHL 400 kV WPP Cibuk - SS Belgrade 50 | 341 | New OHL 400 kV WPP Cibuk - SS Belgrade 50 | 09-2028 | 2 | FALSE | Ahead of time |  | ACTransmissionLine | WPP Cibuk | SS Belgrade 50 | AC | None | 83 | 400 | 0 | 2660 |  |  | 35 | 0 | 0.35 | 5% | ++ | ++ | 0 | 33.75 4.7 | Other Other | Important bird area (IBA), but out of EU territory International Ecological Corridors
1520 | Sofia West (BG) - Nis 2 (RS) 2nd | 342 | Second interconnection line on the border between Bulgaria and Serbia | 09-2034 | 2 | TRUE | Investment on time |  | ACTransmissionLine | SS Sofia West | SS Nis 2 | AC | None | 123 | 400 | 0 | 1330 |  |  | 49 | 0 | 0.49 | 5% | ++ | ++ | 0
1522 | Upgrade of existing OHL 220 kV to 400 kV SS Nis 2 - SS Krusevac 1 | 342 | Upgrade of existing OHL 220 kV to 400 kV SS Nis 2 - SS Krusevac 1 | 09-2034 | 2 | FALSE | Investment on time |  | ACTransmissionLine | SS Nis 2 | SS Krusevac 1 | AC | None | 72 | 400 | 0 | 1330 |  |  | 18 | 0 | 0.18 | 5%
1523 | Upgrading SS 220/110 kV Krusevac 1 to 400 kV | 342 | Upgrading SS 220/110 kV Krusevac 1 to 400 kV | 09-2034 | 2 | FALSE | Investment on time |  | OnshoreSubstation | SS Krusevac 1 | SS Krusevac 1 | AC | None | 0 | 400 | 0 |  |  |  | 6 | 0 | 0.06 | 5%
1524 | Upgrade of existing OHL 220 kV to 400 kV SS Krusevac 1 - SS Kraljevo 3 | 342 | Upgrade of existing OHL 220 kV to 400 kV SS Krusevac 1 - SS Kraljevo 3 | 09-2034 | 2 | FALSE | Investment on time |  | ACTransmissionLine | SS Krusevac 1 | SS Kraljevo 3 | AC | None | 48 | 400 | 0 | 1330 |  |  | 12 | 0 | 0.1 | 5%
1525 | Upgrade of existing OHL 220 kV to 400 kV SS Kraljevo 3 - SY Pozega | 342 | Upgrade of existing OHL 220 kV to 400 kV SS Kraljevo 3 - SY Pozega | 09-2034 | 2 | FALSE | Investment on time |  | ACTransmissionLine | SS Kraljevo 3 | SY Pozega | AC | None | 70 | 400 | 0 | 1330 |  |  | 16.7 | 0 | 0.2 | 5%
1698 | New 400 kV SY Pozega | 342 | New 400 kV SY Pozega | 09-2034 | 2 | FALSE | Investment on time |  | OnshoreSubstation | SS Pozega | SS Pozega | AC | None | 0 | 400 | 0 |  |  |  | 2 | 0 | 0.1 | 5%
1699 | New OHL SS Jagodina 4 - SY Drmno | 342 | New OHL SS Jagodina 4 - SY Drmno | 09-2027 | 2 | FALSE | Ahead of time |  | ACTransmissionLine | SS Jagodina 4 | SY Drmno | AC | None | 95 | 400 | 0 | 2660 |  |  | 26 | 0 | 0.3 | 5% | ++ | ++ | 0
1700 | 400 kV OHL SY Pozega - SS Pljevlja | 342 | Upgrading 220 kV OHL SY Pozega - Vardiste to 2x400 kV and conductoring second circuit on 400 kV OHL SS Bajina Basta - SS Pljevlja from Vardiste to SS Pljevlja. | 09-2034 | 2 | FALSE | Investment on time |  | ACTransmissionLine | SY Pozega | SS Pljevlja | AC | None | 135 | 400 | 0 | 1330 |  |  | 18 | 0 | 0.2 | 5% | ++ | ++ | 0
1701 | 400 kV OHL SY Pozega - SS Visegrad | 342 | Upgrading 220 kV OHL SY Pozega - Vardiste to 2x400 kV and conductoring second circuit on 400 kV OHL SS Bajina Basta - SS Visegrad from Vardiste to SS Visegrad. | 09-2034 | 2 | FALSE | Investment on time |  | ACTransmissionLine | SY Pozega | SS Visegrad | AC | None | 65 | 400 | 0 | 1330 |  |  | 13 | 0 | 0.1 | 5% | ++ | ++ | 0 | 15.7 | OtherNatureProtectionAreasUnderNationalLaw
1532 | New OHL 400 kV Banja Luka - Lika | 343 | New OHL 400 kV Banja Luka - Lika | 12-2033 | 2 | FALSE | Rescheduled | This investment item is postponed due to mutual agreement | ACTransmissionLine | Banja Luka (BA) | Lika (HR) | AC | None | 180 | 400 | 0 |  |  |  | 53 | 0 | 0.0648 | 15%%
1533 | New OHL 400 kV Lika – Melina | 343 | New OHL 400 kV Lika – Melina | 12-2030 | 2 | FALSE | Investment on time |  | ACTransmissionLine | Lika (HR) | Melina (HR) | AC | None | 68 | 400 | 0 |  |  |  | 24.24 | 0 | 0.02448 | 15%%
1534 | New OHL 400 kV Lika – Konjsko | 343 | New OHL 400 kV Lika – Konjsko | 12-2030 | 2 | TRUE | Investment on time |  | ACTransmissionLine | Lika (HR) | Konjsko (HR) | AC | None | 203 | 400 | 0 |  |  |  | 71 | 0 | 0.07308 | 15%%
1535 | New Substation 400/110 kV Lika | 343 | New Substation 400/110 kV Lika | 12-2030 | 2 | FALSE | Investment on time |  | OnshoreSubstation | Lika (HR) | Lika (HR) | AC | None | 0 | 400 | 0 |  |  |  | 11.9 | 0 | 0.1785 | 15%%
1544 | ZuidWest380 Oost | 346 | New 380 kV substation Tilburg; New 380 kV double circuit line 2645MVA between Rilland and Tilburg | 06-2029 | 3 | TRUE | Delayed | Complicated permitting procedures | ACTransmissionLine | Rilland | Tilburg | AC | None | 80 | 380 | 0 |  |  |  | 1090 | 0 | 5.5 | 10%% | ++ | ++ | 0
1638 | Mares Cable : Irish Sea Interconnector Cable | 349 | HVDC 750MW 320kV symmetrical mono-pole interconnector between UKNG and EIRGRID | 07-2027 | 2 | TRUE | Rescheduled |  | DCTransmissionLine | Bodelwyddan | Maynooth | DC | Monopolar | 211 | 320 | 750 |  | VCS |  | 253 | 0 | 0.5 | 15%% | [9 empty] | Given that the actual route of the project might not be defined due to the low degree of maturity of its investment(s), an environmental assessment is not yet available.
1642 | MaresConnect Converter Station Ireland | 349 | 750MW 320kV VSC HVDC Convertor Station to connect to EIRGRID AC | 07-2027 | 2 | FALSE | New Investment |  | OnshoreSubstation | Maynooth | Maynooth | DC | Monopolar | 0 | 320 | 750 |  | VCS |  | 105 | 1 | 3 | 15% | [9 empty] | Given that the actual route of the project might not be defined due to the low degree of maturity of its investment(s), an environmental assessment is not yet available.
1646 | Mares Converter Station UK | 349 | 750MW 320kV VSC HVDC Convertor Station to connect to UKNG | 07-2027 | 2 | FALSE | New Investment |  | OnshoreSubstation | Bodelwyddan | Bodelwyddan | DC | Monopolar | 0 | 320 | 750 |  | VCS |  | 105 | 2 | 3 | 15% | [9 empty] | Given that the actual route of the project might not be defined due to the low degree of maturity of its investment(s), an environmental assessment is not yet available.
1652 | Enabling Works 1: 1 x 400kV Connection bay UKNG and associated works | 349 | AC Connection to UKNG system Bodelwyddan 400kV bays and associated works | 07-2027 | 2 | FALSE | New Investment |  | OnshoreSubstation | Bodelwyddan | Bodelwyddan | AC | None | 0 | 245 | 0 |  |  |  | 5 | 2 | 0.005 | 15%% | [9 empty] | Given that the actual route of the project might not be defined due to the low degree of maturity of its investment(s), an environmental assessment is not yet available.
1653 | Enabling Works 2: EIRGRID 1 x 245kV Connection bay at Maynooth and associated works | 349 | EIRGRID 1 x 245kV Connection bays at Maynooth and associated works | 07-2027 | 2 | FALSE | New Investment |  | OnshoreSubstation | Maynooth | Maynooth | AC | None | 0 | 245 | 0 |  |  |  | 5 | 2 | 0.005 | 15%% | [9 empty] | Given that the actual route of the project might not be defined due to the low degree of maturity of its investment(s), an environmental assessment is not yet available.
1622 | 400kV OHL SS Bitola - SS Elbasan | 350 | New 150km cross-border single circuit 400kV OHL between existing substation Bitola(Macedoonia) and Elbasan(Albania). | 12-2023 | 4 | TRUE | New Investment |  | ACTransmissionLine | Bitola | Elbasan | AC | None | 151 | 400 | 0 |  |  |  | 63.733 | 0 | 2.867 | ±10%
1623 | 400 kV SS Ohrid | 350 | New 400/110 kV substation in Ohrid area connected in/out to the new 400 kV line Bitola-Elbasan. This SS will contribute to the security of supply in the internal southern network of the country. | 12-2023 | 4 | FALSE | New Investment |  | OnshoreSubstation | SS Ohrid | missing value | AC | None | 0 | 400 | 0 |  |  |  | 17.68 | 0 | 1.414 | ±10%
1555 | Lienz (AT) - Veneto region (IT) | 375 | Reconstruction of the existing 220kV-interconnection line between Lienz and Veneto Region (IT) | 12-2035 | 2 | TRUE | New Investment |  | ACTransmissionLine | Lienz (AT) | Veneto region (IT) | AC | None | 140 | 220 | 0 | 900 |  |  | 140 | 0 | 0.42 | 10% | ++ | ++ | 0 | 31 | Other | - | 3 | Other | -
1559 | Refurbishment of the 400kV Meliti (GR)-Bitola (MK) interconnector | 376 | Reconductoring of the existing 400kV interconnection line Meliti (GR)-Bitola (MK) | 06-2035 | 1 | TRUE | Investment on time |  | ACTransmissionLine | Meliti (GR) | Bitola (MK) | AC | None | 35.512 | 400 | 0 |  |  |  | 5.625 | 0 | 0.215 | ±20%%
1561 | BE-NL interconnector: upgrade VanEyck-Maasbracht | 377 | Upgrade of existing interconnection between Van Eyck (BE) and Maasbracht (NL), by adding PST(s) and/or replacing existing conductors by HTLS. The study is to confirm the appropriate implementation option and phasing of this implementation also with respect to evolution of DE-NL interconnectors. | 12-2032 | 1 | TRUE | Rescheduled | The project has been rescheduled to be in line with the timing of other grid reinforcements to be compliant with the Clean Energy Package. | ACTransmissionLine | VanEyck | Maasbracht | AC | None | 12 | 380 | 0 | 2600 |  |  | 71 | 0 | 0.1 | 25%% | - | - | 0
1584 | Transformer Gatica | 378 | Only 400 to 220 kV transformer. Not the whole substation | 12-2027 | 2 | TRUE | Rescheduled |  | OnshoreSubstation | GATICA 400 | GATICA 220 | AC | None | 0 | 220 | 0 | 600 |  |  | 8.16 | 0 | 0.1224 | 10%%
1593 | Uprate Gatica-Guenes | 379 | Uprate 400 kV Gatica-Guenes substation | 12-2026 | 2 | TRUE | Investment on time |  | ACTransmissionLine | Gatica | Guenes | AC | None | 38.8 | 400 | 0 |  |  |  | 0.22 | 0 | 0.0033 | 10%%
1595 | Uprate Gatica-Amorebieta-Ichaso | 379 | Uprate the 400 kV axis Gatica-Amorebieta-Ichaso | 12-2026 | 2 | FALSE | Investment on time |  | ACTransmissionLine | Gatica | Ichaso | AC | None | 69.12 | 400 | 0 |  |  |  | 1.65 | 0 | 0.02475 | 10%%
1597 | Uprate Gatica-Azpeitia | 379 | Uprate the 400 kV Gatica-Azpeitia line | 12-2026 | 2 | FALSE | Investment on time |  | ACTransmissionLine | Gatica | Azpeitia | AC | None | 57 | 400 | 0 |  |  |  | 0.31 | 0 | 0.00465 | 10%%
1692 | HVDC from Wilhelmshaven to Region Hamm | 1034 | HVDC line from Wilhelmshaven to Uentrop to integrate onshore and offshore wind energy in Northern Germany and transport it to the load centers in Western Germany | 12-2031 | 2 | TRUE | Delayed | explanation missing | DCTransmissionLine | Wilhelmshaven | Region Hamm | DC | Bipolar | 270 | 525 | 2000 |  | VCS |  | 2995 | 0 | 18.7 | 10%
1693 | HVDC from Heide/West to Polsum | 1034 | HVDC line from Heide/West to Polsum to integrate onshore and offshore wind energy in Northern Germany and transport it to the load centers in Western Germany | 12-2031 | 2 | FALSE | Investment on time |  | DCTransmissionLine | Heide/West | Polsum | DC | Bipolar | 440 | 525 | 2000 |  | VCS |  | 4060 | 0 | 30.8 | 10%
1675 | SE North-south Long-term reinforcements | 1039 | Reactive measures in substations and series compensations in order to increase capacity between SE2 and SE3. Replacement of ageing overhead lines that also will contribute to the increased capacity. The need for capacity is driven by RES integration in northern Sweden and nuclear decommission in southern Sweden. | 01-2040 | 1 | TRUE | Investment on time |  | ACTransmissionLine | SE2 | SE3 | AC | None | 475 | 400 | 0 |  |  |  | 1250 | 0 | 0.5 | +-10%% | ++ | ++ | 0
1764 | SE North-south Long-term reinforcements | 1039 | The second investment has also the same description as the first one. | 01-2040 | 1 | TRUE | Investment on time |  | ACTransmissionLine | SE2 | SE3 | AC | None | 475 | 400 | 0 |  |  |  | 1250 | 0 | 0.5 | +-10%%
1677 | LirIC | 1040 | New HVDC VSC Monopole sub sea cable between Kilroot 275kV substation in Northern Ireland (TBC) and Kilmarnock South 400kV sub station in Scotland (TBC) | 12-2028 | 1 | TRUE | New Investment | N/A | OffshoreDCTransmissionCable | NI Kilroot 275kV (TBC) | GB Kilmarnock South 400kV (TBC) | DC | Monopolar | 133 | 320 | 700 |  | VCS |  | 446 | 0 | 9.93 | 20% | ++ | ++ | + (between sync areas)
1682 | Wadi El Natroon - Mesogeia / St Stefanos HVDC | 1041 | Wadi El Natroon - Mesogeia / St Stefanos HVDC Link. This investment includes two VSC converter stations at both ends of the bipolar 525kV HVDC link along with the grounding electrodes. The interconnection circuits consist of approximately 500km of overhead HVDC lines (ACSR/PLOVER), approximately 30km length of underground cables (Al 2200mm2) and approximately 921 or 954 km of submarine Cables (Al 1800mm2). | 01-2028 | 1 | TRUE | Investment on time |  | DCTransmissionLine | Wadi El Natroon | Mesogeia / St Stefanos | DC | Bipolar | 1472 | 525 | 3000 |  | VCS |  | 3569 | 0 | 53.535 | 10% | ++ | ++ | + (between sync areas) | 83 | HabitatsDirective |  | 18.5 | HabitatsDirective
1779 | Offshore Wind LT 1 | 1042 | 'Connection of 700 MW offshore wind farms to onshore Darbenai substation. Offshore platform and cables planned to be build and owned not by TSO, therefore their costs are not added to this project investments. | 12-2028 | 2 | TRUE | New Investment |  | OnshoreSubstation | Darbenai | offshore platform | AC | None | 70 | 220 | 0 |  |  |  | 20 | 0 | 0.15 | +10%, -10%% |  |  |  | 0.01 7.8 7.8 | HabitatsDirective BirdsDirective OtherNatureProtectionAreasUnderNationalLaw
1688 | Nuojuankangas-Huutokoski (Järvilinja 2) | 1046 | New single circuit 400 kV OHLs will be built from central part of Finland to the northern area to increase the capacity between North and South Finland. Enables integration of renewables to the northern part of the country. | 06-2026 | 2 | TRUE | New Investment |  | ACTransmissionLine | Nuojuankangas | Huutokoski | AC | None | 290 | 400 | 0 | 2200 |  |  | 140 | 0 | 0.15 | +- 20% | ++ | ++ | 0
1689 | Petäjäskoski-Herva-Nuojuankangas | 1046 | New single circuit 400 kV OHL will be built to the northern part of Finland. Enables the integration of renewables to the northern part of the country and the increasing power transfer from North to South . | 06-2027 | 3 | FALSE | New Investment |  | ACTransmissionLine | Petäjäskoski | Nuojuankangas | AC | None | 215 | 400 | 0 | 2200 |  |  | 80 | 0 | 0.15 | +-20% | ++ | ++ | 0
1697 | Petäjävesi/Toivila-Hikiä (2 x OHL) | 1046 | New 2 x 400 kV OHL will be built to the central part of Finland (+other required investments). Enables the integration of renewables and the utilization of full transfer capacity from North to South . | 06-2028 | 2 | FALSE | New Investment |  | ACTransmissionLine | Petäjävesi/Toivila | Hikiä | AC | None | 175 | 400 | 0 | 2200 |  |  | 90 | 0 | 0.15 | +-20% | ++ | ++ | 0
1780 | Jylkkä-Alajärvi (2 x OHL) –Toivila (1 x OHL) | 1046 | New 2 x 400 kV OHL built from Jylkkä substation (western Finland) to Alajärvi substation (central Finland) (+other required investments). The line continues as a single 400 kV OHL from Alajärvi to Toivila substation (Central Finland). Enables the integration of renewables and the utilization of full transfer capacity from North to South . | 06-2028 | 2 | FALSE | New Investment |  | ACTransmissionLine | Jylkkä | Toivila | AC | None | 300 | 400 | 0 | 2200 |  |  | 140 | 0 | 0.15 | +-20%
1781 | Nuojuankangas-Petäjävesi (Metsälinja 2) | 1046 | New single circuit 400 kV OHL will be built to the central part of Finland. Enables the integration of renewables and the utilization of full transfer capacity from North to South . | 06-2030 | 2 | FALSE | New Investment |  | ACTransmissionLine | Nuojuankangas | Petäjävesi | AC | None | 290 | 400 | 0 | 2200 |  |  | 120 | 0 | 0.15 | +-20%
1691 | Emden-Eemshaven | 1047 | Increase of the interconnection capacity between the Netherlands (Eemshaven) and Germany (Emden) by adding a new 380kV transmission line. The project is planned as a combination of overhead line, onshore cable and sub sea cable and a PST in Emden. | 12-2035 | 1 | TRUE | Investment on time |  | OffshoreACTransmissionCable | Emden | Eemshaven | AC | None | 31 | 380 | 0 |  |  |  | 200 | 0 | 1.6 | +-10%%
1709 | Greece Africa Power Interconnector | 1048 | 2 HVDC Subsea cables interconnecting the Northern coast of Egypt with the island of Crete at Atherinolakkos. At both connection points bipolar HVDC conversion stations will be constructed for the connection to the national HV grids. | 01-2028 | 1 | TRUE | Investment on time |  | OffshoreDCTransmissionCable | Atherinolakkos (Crete) | Mersa Matruh | DC | Bipolar | 450 | 500 | 2000 |  | VCS |  | 1300 | 6 | 12 | 5%% | ++ | ++ | + (between sync areas) |  |  |  |  | None
1706 | Converter Stations & Subsea Cabling | 1049 | 1.4 GW HVDC electricity interconnector between UK and Belgium Voltage Source Converter (VSC)/Bipolar Grid connection point (substations name): Kemsley (UK) and near Zeebrugge (Belgium), exact substation location subject to grid study in Belgium. Total cable length (substation to substation) 230km (1km in UK and 30km in France) Two cables (XLPE) laid in a single trench Nominal voltage: ±525 kV Thermal limit (Imax): 1330 A Mvar capability range at terminals: 460 MVAr Bus-bar to bus-bar losses profile over MW range: 2.3% (33 MW) full load; 0% (0 MW) at zero load. The annual Availability is 98.1% availability, with 1.8% planned outages, and 0.1% forced outages. The maximum single failure according to the design is 1.4GW. The project will enable the reduction of CO2 emissions by substituting electricity from fossil fuels by generation from RES and nuclear power. There are no material anticipated environmental impacts during construction and operation. | 12-2029 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | Kemsley, Kent | Kemsley, Kent | DC | Bipolar | 230 | 525 | 1400 |  | VCS |  | 937 | 65 | 35 | 6% | ++ | ++ | + (between sync areas) | 1 1 | RAMSARSite HabitatsDirective |  |  | None |  | No other residual impact
1707 | Converter stations and Subsea Cabling | 1050 | 1.4 GW HVDC electricity interconnector between UK and Germany Voltage Source Converter (VSC)/Bipolar Grid connection point (substations name): Corringham (UK) and near Emden (Germany), exact substation location subject to grid study in Germany. Total cable length (substation to substation) 610km (35km in UK and 25km in Germany) Two cables (XLPE) laid in a single trench Nominal voltage: ±525 kV Thermal limit (Imax): 1330 A Mvar capability range at terminals: 460 MVAr Bus-bar to bus-bar losses profile over MW range: 2.3% (33 MW) full load; 0% (0 MW) at zero load. The annual Availability is 98.1% availability, with 1.8% planned outages, and 0.1% forced outages. The maximum single failure according to the design is 1.4GW. The project will enable the reduction of CO2 emissions by substituting electricity from fossil fuels by generation from RES and nuclear power. There are no material anticipated environmental impacts during construction and operation | 12-2030 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | Corringham, Essex | East Anglia, connection node 400kV Substation | DC | Bipolar | 610 | 525 | 1400 |  | VCS |  | 1675 | 65 | 37 | 3%% |  |  |  | 9 12 | HabitatsDirective MarinStrategyFrameworkDirective |  |  | None
1708 | Converter stations and Subsea cables | 1051 | 1.4 GW HVDC electricity interconnector between UK and Germany Voltage Source Converter (VSC)/Bipolar Grid connection point (substations name): Norwich Main (UK) and near Revsing (Denmark), exact substation location subject to grid study in Denmark. Total cable length (substation to substation) 610km (35km in UK and 25km in Germany) Two cables (XLPE) laid in a single trench Nominal voltage: ±525 kV Thermal limit (Imax): 1330 A Mvar capability range at terminals: 460 MVAr Bus-bar to bus-bar losses profile over MW range: 2.3% (33 MW) full load; 0% (0 MW) at zero load. The annual Availability is 98.1% availability, with 1.8% planned outages, and 0.1% forced outages. The maximum single failure according to the design is 1.4GW. The project will enable the reduction of CO2 emissions by substituting electricity from fossil fuels by generation from RES and nuclear power. There are no material anticipated environmental impacts during construction and operation. | 12-2031 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | Norwich Main | Mablethorpe, Lincolnshire | DC | Bipolar | 640 | 525 | 1400 |  | VCS |  | 1471 | 65 | 37 | 6% |  |  |  | 1 18 | HabitatsDirective MarinStrategyFrameworkDirective
1713 | Lienz (AT) - Obersielach (AT) | 1052 | upgrade from 220 kV to 380 kV | 06-2032 | 2 | TRUE | Rescheduled | Revision of the grid expansion concept. Cascade effects due to project delays in projects ranked ahead. | ACTransmissionLine | Lienz (AT) | Obersielach (AT) | AC | None | 170 | 380 | 0 |  |  |  | 500 | 0 | 1.4 | 10% |  |  |  | 4 | None |  | 81 | None
1715 | Westtirol (AT) - Zell/Ziller (AT) | 1054 | Upgrade of the existing 220kV-line Westtirol - Zell-Ziller and erection of an additional 220/380kV-Transformer. Line length 105km. | 12-2029 | 2 | TRUE | Rescheduled | Revision of the expansion concept. Cascade effects due to project delays in projects ranked ahead. | ACTransmissionLine | Westtirol (AT) | Zell-Ziller (AT) | AC | None | 105 | 220 | 0 |  |  |  | 54 | 0 | 0.16 | 10% |  |  |  | 11 | None |  | 74 | None
1716 | Interconnection between Crete and Peloponnese (Phase I) | 1055 | New 150 kV AC double circuit submarine and underground cables between Crete and Peloponnese | 05-2021 | 6 | FALSE | Rescheduled |  | ACTransmissionLine | Chania I | Molai (through Sklavouna Terminal) | AC | None | 179 | 150 | 0 |  |  |  | 376 | 0 | 1.2 | 9% | ++ | ++ | 0 | 25 11 2 | HabitatsDirective BirdsDirective OtherNatureProtectionAreasUnderNationalLaw |  | 9.63 | HabitatsDirective
1717 | Interconnection between Crete and Attica (Phase II) | 1055 | New symmetric bipolar submarine HVDC-VSC link between Crete and Attica | 06-2024 | 4 | TRUE | Rescheduled |  | DCTransmissionLine | Damasta | Koumoundouros | DC | Bipolar | 373 | 500 | 1000 |  | VCS |  | 1040 | 0 | 1.5 | 9% | ++ | ++ | + (between sync areas) | 5.2 4.48 | HabitatsDirective OtherNatureProtectionAreasUnderNationalLaw |  | 14.9 | HabitatsDirective
1726 | HVDC Line DE-CH | 1058 | The concept of extending German HVDC-Lines towards Switzerland and Italy offers a further potential to realize a new North-South HVDC corridor. Large developments of variable wind and photovoltaic power, coal and nuclear phaseout, mainly gas-based thermal generation, and the pump storage po-tentials in the Alps are the main drivers of power system evolution that will challenge the future trans-mission system in central southern Europe. | 12-2037 | 1 | TRUE | Rescheduled |  | DCTransmissionLine | Oberjettingen (DE) | Mettlen (CH) | DC | Bipolar | 250 | 400 | 1000 |  | VCS |  | 1500 | 0 | 12 | ±20%% |  |  |  | 0 | Other |  | 0 | Other
645 | OHL between the Laino and Altomonte in Calabria | 1059 | New 400kV OHL between the existing substations of Laino and Altomonte in Calabria (investment previously included in P127). | 12-2029 | 3 | FALSE | Delayed | Delay due to permitting reasons. | ACTransmissionLine | Laino (IT) | Altomonte (IT) | AC | None | 50 | 400 | 0 | 2078 |  |  | 203 | 0 | 0.9 | 0% | ++ | ++ | 0 | 9 | Other |  | 1 | Other
1727 | Montecorvino-Avellino and Nord-Ben. in Campania | 1059 | New 400 kV between Montecorvino-Avellino and Nord-Ben. in Campania | 12-2028 | 3 | TRUE | New Investment |  | ACTransmissionLine | Montecorvino (IT) | Benevento (IT) | AC | None | 0 | 400 | 0 | 1870 |  |  | 319 | 0 | 0.99 | 0% | ++ | ++ | 0 | 24 | Other |  | 5 | Other
1736 | 400kV OHL, Maritsa East 2 (BG) – Vize Havza (TR) | 1066 | New interconnection line BG-TR by a 150km single circuit 400kV OHL. | 07-2036 | 1 | TRUE | New Investment |  | ACTransmissionLine | Maritsa East 2 (BG) | Vize Havza (TR) | AC | None | 150 | 400 | 0 |  |  |  | 60 | 0 | 1.2 | +-10%%
1738 | New AC 400 kV interconnection line Greece - Turkey | 1067 | New AC 400 kV Overhead line Greece - Turkey | 06-2035 | 1 | TRUE | Investment on time |  | ACTransmissionLine | Nea Santa (GR) | Babaeski (TR) | AC | None | 130 | 400 | 0 |  |  |  | 32.55 | 0 | 0.64 | ± 10%% | ++ | ++ | 0
1787 | New 400 kV OHL Nea Santa - Filippi | 1067 | New AC 400 kV double circuit OHL Nea Santa - Filippi | 12-2027 | 2 | FALSE | New Investment |  | ACTransmissionLine | Nea Santa | Fillipi | AC | None | 140 | 400 | 0 |  |  |  | 49 | 0 | 0.5 | ± 10%% | ++ | ++ | 0
1740 | LaSGo Link - Gotland to Latvia | 1068 | New monopolar HVDC VSC monopole sub-sea cable running from a new substation in Gotland (TBC) to Grobina in Latvia (or Ventspils or a possible a new substation inbetween Grobina and Ventspils) (TBC). This investment consists of two VSC HVDC converter stations connected via two 320kV HVDC XLPE cables. | 06-2031 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | New substation on Gotland (TBC) | Grobina (TBC) | DC | Monopolar | 195 | 320 | 500 |  | VCS |  | 511.5 | 0 | 8 | +/-15%% | ++ | ++ | + (between sync areas)
1741 | LaSGo Link - Sweden to Gotland | 1068 | New monopolar HVDC VSC monopole sub-sea cable running from the vicinity of Oskarshamn in mainland Sweden (TBC) to a new substation in Gotland (TBC). This investment consists of one HVDC VSC converter station connected via two 320kV HVDC XLPE cables to a Converter Station being built as part of the LaSGo Link Gotland to Latvia investment. | 06-2031 | 1 | FALSE | New Investment |  | OffshoreDCTransmissionCable | Oskarshamn (TBC) | New substation on Gotland (TBC) | DC | Monopolar | 125 | 320 | 700 |  | VCS |  | 287.5 | 0 | 4 | +/-15%% | ++ | ++ | + (between sync areas)
1742 | 400 kV OHL SS Subotica 3 – SS Sándorfalva | 1074 | New 400 kV interconnection OHL between SS Subotica (RS) and SS Sándorfalva (HU). This is the main investment of the project and a part of the new North-South corridor for energy transmission. | 09-2033 | 1 | TRUE | Ahead of time | No delay on this investment yet. | ACTransmissionLine | SS Subotica 3 | SS Sándorfalva | AC | None | 50.6 | 400 | 0 | 1330 |  |  | 24.1 | 0 | 0.24 | 10% | ++ | ++ | 0
1743 | 400 kV OHL SS Sombor 3 – SS Srbobran | 1074 | New 400 kV OHL from existing substation Sombor 3 to existing substation Srbobran (both in Serbia). | 09-2033 | 1 | FALSE | Ahead of time | No delay on this investment yet. | ACTransmissionLine | SS Sombor 3 | SS Srbobran | AC | None | 80 | 400 | 0 | 1330 |  |  | 19.5 | 0 | 0.2 | 5% | ++ | ++ | 0
1744 | 400 kV OHL SS Srbobran – SS Sremska Mitrovica 2 | 1074 | New 400 kV OHL from existing substation Srbobran to existing substation Sremska Mitrovica 2 (both in Serbia). | 09-2033 | 1 | FALSE | Ahead of time | No delay on this investment yet. | ACTransmissionLine | SS Srbobran | SS Sremska Mitrovica 2 | AC | None | 90 | 400 | 0 | 1330 |  |  | 21.2 | 0 | 0.21 | 5% | ++ | ++ | 0
1750 | Sea-Socket | 1082 | Floating substation platform facilitating 700-MW multiple offshore wind connections and transmitted via 220kV subsea AC cables to onshore substation(s) located along the Shannon Estuary | 01-2035 | 1 | TRUE | New Investment |  | OffshoreSubstation | New substation connection to 400kV/220kV lines in the Shannon Estuary | Not applicable - offshore connection point at Sea-Socket Platform | AC | None | 40 | 220 | 0 |  |  |  | 375 | 20 | 3 | 25%%
1751 | Malta-Italy Cable link No. 2 | 1085 | 200MWe HVAC 2nd electrical cable link between Malta and Sicily | 12-2025 | 1 | TRUE | New Investment |  | OffshoreACTransmissionCable | In Malta (MT): Maghtab Terminal Station (Maghtab TS) | In Italy (IT): Ragusa Terminal Station (Ragusa TS) | AC | None | 117.5 | 220 | 0 |  |  |  | 170 | 0 | 2.7 | 20% | ++ | ++ | 0
1752 | L356 Mustvee-Paide 330 kV OHL reconstrucion (EE) | 1086 | The new reconstructed 330 kV OHL will be wired with 3x402 mm2 in phase and with operating temperature of 80 degrees Celsius. To reduce the environmental impact partially the parallel 110 kV lines will be place on the common towers with 330 kV reconstructed line. The thermal transmission capacity of the line is planned 1770 MW. | 12-2025 | 2 | TRUE | New Investment |  | ACTransmissionLine | Mustvee | Paide | AC | None | 87 | 330 | 0 | 1770 |  |  | 24 | 24 | 0.12 | 10% | ++ | ++ | 0 | 0.8 | HabitatsDirective |  | 1.03 | HabitatsDirective
1753 | L357 Kiisa-Paide 330 kV OHL reconstruction (EE) | 1086 | The new reconstructed 330 kV OHL will be wired with 3x402 mm2 in phase and with operating temperature of 80 degrees Celsius. To reduce the environmental impact partially the parallel 110 kV lines will be place on the common towers with 330 kV reconstructed line. The thermal transmission capacity of the line is planned 1770 MW. | 12-2026 | 2 | FALSE | New Investment |  | ACTransmissionLine | Kiisa | Paide | AC | None | 70 | 330 | 0 | 1770 |  |  | 19 | 19 | 0.1 | 10% | ++ | ++ | 0 | 3.3 | OtherNatureProtectionAreasUnderNationalLaw |  | 1.95 | HabitatsDirective
1754 | Lihula 330 KV substation (EE) and reinforcement of internal grid in western part of Estonia | 1086 | New Lihula 330 kV substation will be connected to existing Harku-Sindi 330 kV OHL in Lihula. It consists of 2 330 kV duplex bays for 330 kV lines, and 3 simplex 330 kV bays of which 2 will be used for power transformers (200 MVA each) and one for reactive power compensator (125 Mvar). The investment also includes the reinforcement of internal 110 kV grid where are the potential RES connection points. | 12-2025 | 2 | FALSE | New Investment |  | OnshoreSubstation | Lihula | Lihula | AC | None | 0 | 330 | 0 |  |  |  | 26 | 26 | 0.13 | 10%
1755 | The interconnector between Latvia and Estonia with Off-shore wind connection hub in between | 1088 | The planned subsea interconnection between Estonia and Latvia with off-shore connection hub in between. The connection of off-shore wind up to 1000 MW. | 12-2030 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | Tume (LV) | Sindi (EE) | DC | Bipolar | 180 | 450 | 1000 |  | VCS |  | 460 | 0 | 2 | 20% | ++ | ++ | + (between sync areas)
1756 | Cross-border network reinforcement Grobina (LV) - Derbenai (LT) | 1088 | The reconstruction of the existing 330 kV OHL from substation Grobina in Latvia to substation Derbenai in Lithuania. The capacity increase on cross-border Latvia - Lithuania up to 300 MW. | 12-2025 | 1 | FALSE | New Investment |  | ACTransmissionLine | Grobina (LV) | Derbenai (LT) | AC | None | 85 | 330 | 0 |  |  |  | 25 | 0 | 0.5 | +5%; -5%% | ++ | ++ | 0
1757 | Cross-border network reinforcement Broceni (LV) - Telsiai (LT) | 1088 | 330 kV OHL | 12-2030 | 1 | FALSE | New Investment |  | ACTransmissionLine | Broceni (LV) | Telsiai (LT) | AC | None | 90 | 330 | 0 |  |  |  | 25 | 0 | 0.5 | +5%; -5%% | ++ | ++ | 0
1758 | Internal network reinforcement Ventspils (LV) - Broceni (LV) | 1088 | 330 kV OHL | 12-2030 | 1 | FALSE | New Investment |  | ACTransmissionLine | Ventspils (LV) | Broceni (LV) | AC | None | 105 | 330 | 0 |  |  |  | 50 | 0 | 0.5 | +5%; -5%% | ++ | ++ | 0
1761 | Off-shore substation for off-shore wind park connection | 1088 | The planned off-shore substation in Baltic Sea on cross-border between Estonia and Latvia. The amount and location of the substation(s) will be determined by studies. | 12-2030 | 1 | TRUE | New Investment |  | OffshoreSubstation | ELWIND off-shore substation | ELWIND off-shore substation | DC | Bipolar | 0 | 450 | 1000 |  | VCS |  | 300 | 0 | 3 | 20% | ++ | ++ | + (between sync areas)
1759 | Connection between Belgium and the Danish Energy Island | 1092 | Hybrid HVDC interconnector | 12-2031 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | Mercator | Substation on Danish Energy Island | DC | Bipolar | 773 | 1050 | 2000 |  | VCS |  | 2430 | 0 | 12 | 20% | ++ | ++ | + (between sync areas)
1777 | Connection between Denmark and the Danish Energy Island | 1092 | Hybrid HVDC interconnector | 12-2030 | 1 | FALSE | New Investment |  | OffshoreDCTransmissionCable | Danish Energy Island | Revsing | DC | Bipolar | 140 | 1050 | 1400 |  | VCS |  | 1160 | 0 | 6 | 20% | ++ | ++ | + (between sync areas)
1760 | Estlink 3 | 1094 | HVDC subsea connection between FI and EE | 06-2040 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | FI | EE | DC | None | 100 | 450 | 700 |  | VCS |  | 500 | 0 | 0.75 | 20% | ++ | ++ | + (between sync areas)
1769 | Estonian grid reinforcements: L346 Paide-Sopi 330 kV OHL reconstruction | 1094 | The new reconstructed 330 kV OHL will be wired with 3x402 mm2 in phase and with operating temperature of 80 degrees Celsius. The thermal transmission capacity of the line is planned 1772 MW. | 12-2028 | 2 | FALSE | New Investment |  | ACTransmissionLine | Paide | Sopi | AC | None | 66.3 | 330 | 0 | 1770 |  |  | 18.2 | 18.2 | 0.09 | 10% | ++ | ++ | 0
1770 | Estonian grid reinforcements: L347 Sopi-Sindi 330 kV OHL reconstruction | 1094 | The new reconstructed 330 kV OHL will be wired with 3x402 mm2 in phase and with operating temperature of 80 degrees Celsius. The thermal transmission capacity of the line is planned 1772 MW. | 12-2028 | 2 | FALSE | New Investment |  | ACTransmissionLine | Sopi | Sindi | AC | None | 28.7 | 330 | 0 | 1770 |  |  | 6.1 | 6.1 | 0.03 | 10% | ++ | ++ | 0
1771 | Estonian grid reinforcements: L506 Rakvere-Kiisa 330 kV OHL reconstruction | 1094 | The new reconstructed 330 kV OHL will be wired with 3x402 mm2 in phase and with operating temperature of 80 degrees Celsius. The thermal transmission capacity of the line is planned 1772 MW. | 12-2029 | 2 | FALSE | New Investment |  | ACTransmissionLine | Rakvere | Kiisa | AC | None | 107.8 | 330 | 0 | 1770 |  |  | 34.6 | 34.6 | 0.17 | 10% | ++ | ++ | 0
1774 | Estonian grid reinforcements: L360 Püssi-Rakvere 330 kV OHL reconstruction | 1094 | The new reconstructed 330 kV OHL will be wired with 3x402 mm2 in phase and with operating temperature of 80 degrees Celsius. The thermal transmission capacity of the line is planned 1772 MW. | 12-2030 | 2 | FALSE | New Investment |  | ACTransmissionLine | Püssi | Rakvere | AC | None | 57.7 | 330 | 0 | 1770 |  |  | 18.2 | 18.2 | 0.09 | 10% | ++ | ++ | 0
1775 | Estonian grid reinforcements: L512 Aruküla-Kiisa 330 kV new OHL | 1094 | The new 330 kV OHL will be wired with 3x402 mm2 in phase and with operating temperature of 80 degrees Celsius. The thermal transmission capacity of the line is planned 1772 MW. | 12-2030 | 2 | FALSE | New Investment |  | ACTransmissionLine | Aruküla | Kiisa | AC | None | 32.3 | 330 | 0 | 1770 |  |  | 12.6 | 12.6 | 0.06 | 10% | ++ | ++ | 0
1785 | Inkoo-Hikiä | 1094 | Inkoo-Hikiä 400 kV single circuit OHL | 06-2040 | 1 | FALSE | New Investment |  | ACTransmissionLine | Inkoo (FI) | Hikiä (FI) | AC | None | 100 | 400 | 0 | 2200 |  |  | 40 | 0 | 0 | +-20% | ++ | ++ | 0
1762 | 4th AC Finland-Sweden north | 1095 | Fourth AC 400 kV overhead line interconnector between Finland north and Sweden SE1. | 06-2035 | 1 | TRUE | New Investment |  | ACTransmissionLine | FI | SE1 | AC | None | 250 | 400 | 0 | 2200 |  |  | 270 | 0 | 0.3 | +-20%% | ++ | ++ | 0
1763 | Beznau - Mettlen | 1096 | line | 12-2028 | 3 | TRUE | Investment on time |  | ACTransmissionLine | Beznau | Mettlen | AC | None | 1 | 380 | 0 |  |  |  | 92.92 | 0 | 0.46 | 10% | ++ | ++ | 0 | 0 | Other |  | 47 | Other
1765 | Upgrade to Konti-Skan | 1097 | This project will increase the capacity on the existing HVDC connections Konti-Skan 1 and 2 connecting SE3 and DK1 by 700 MW, resulting in a total of 1400 MW capacity between SE3 and DK1. | 01-2032 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | SE4 (Substation is not decided yet) | DK1 (Substation is not decided yet) | DC | None | 160 | 525 | 700 |  | VCS |  | 317 | 0 | 1 | +-20%% | ++ | ++ | + (between sync areas)
1778 | Offshore Wind LT 2 | 1098 | Offshore platform for connection of up to 700 MW offshore wind farms, 220 kV subsea cables to onshore substation, internal grid reinforcements in onshore network. | 12-2030 | 1 | TRUE | New Investment |  | OffshoreSubstation | Darbenai | offshore platform | AC | None | 70 | 220 | 0 |  |  |  | 270 | 0 | 4.05 | 9% | ++ | ++ | 0
1788 | New 330 kV OHL Darbenai-Musa | 1098 | New 330 kV OHL to strengthen internal network after connection of 700 MW offshore capacity. | 12-2030 | 1 | FALSE | New Investment |  | ACTransmissionLine | Darbenai | Musa | AC | None | 170 | 330 | 0 | 943 |  |  | 66 | 0 | 0.296 | +5%, - 5%% | ++ | ++ | 0
1789 | New 330 kV OHL Panevezys-Musa | 1098 | New 330 kV OHL to strengthen internal network after connection of 700 MW offshore capacity. | 12-2030 | 1 | FALSE | New Investment |  | ACTransmissionLine | Panevezys | Musa | AC | None | 72 | 330 | 0 | 943 |  |  | 21.6 | 0 | 0.125 | +5%, - 5%% | ++ | ++ | 0
1766 | Modernization of existing interconnector Hradec - Röhrsdorf | 1100 | The project consists in the modernization of an existing 400 kV line between the Hradec and Röhrsdorf substations. | 08-2028 | 3 | TRUE | New Investment |  | ACTransmissionLine | Hradec | Röhrsdorf | AC | None | 81.5 | 400 | 0 | 1694 |  |  | 44.512 | 0 | 0.01 | -10%, +15%% | ++ | ++ | 0 | 13 7.5 | BirdsDirective HabitatsDirective |  | 3 | IUCNKeyBiodiversityAreas
1767 | Mettlen - Ulrichen | 1102 | AC Line | 12-2035 | 3 | TRUE | Investment on time |  | ACTransmissionLine | Mettlen | Ulrichen | AC | None | 1 | 380 | 0 |  |  |  | 290.22 | 0 | 1.45 | 10% | ++ | ++ | 0 | 0 | Other |  | 34 | Other
1768 | Bickigen - Chippis | 1103 | line | 12-2028 | 3 | TRUE | Investment on time |  | ACTransmissionLine | Bickigen | Chippis | AC | None | 1 | 380 | 0 | 915 |  |  | 48.75 | 0 | 0.24 | 10% | ++ | ++ | 0 | 0 | Other |  | 0 | Other
1772 | Roost - Flebour - Bauler | 1104 | Upgrade of existing transmission OHL between Roost and Bauler to increase the thermal cross-border capacity. | 12-2027 | 2 | TRUE | New Investment |  | ACTransmissionLine | Bauler (DE) | Roost (LU) | AC | None | 27.8 | 220 | 0 |  |  |  | 14.75 | 0 | 0.118 | 10%% | ++ | ++ | 0
1773 | Bauler - Niederstedem | 1104 | Upgrade of existing transmission OHL between Bauler and Niederstedem to increase the thermal capacity. To reach a higher capacity the options are High Temperature Low Sag (HTLS) conductors or a reconstruction of the tie-line in the existing route . | 12-2030 | 2 | FALSE | New Investment |  | ACTransmissionLine | Niederstedem (DE) | Bauler (DE) | AC | None | 20.3 | 220 | 0 |  |  |  | 50 | 0 | 0.4 | 10% | ++ | ++ | 0
1782 | Black Sea HVDC submarine interconnection project | 1105 | Submarine cable Anaklia-Constanta Sud which will be placed under Black Sea DC 2-circuit ±500 kV cable, route distance – 1100KM | 12-2029 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | SS Anaklia | SS Constanta Sud | DC | Bipolar | 1100 | 500 | 1000 |  | VCS |  | 2118.85 | 0 | 9.42 | 5% | ++ | ++ | + (between sync areas)
1793 | Bornholm Energy Island: BEI-DKE | 1106 | DC connection from mainland Zealand (Solhøjgård, DKE) to Bornholm including converters on Zealand and on Bornholm, as well as AC and MTDC components on the island of Bornholm | 12-2029 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | Solhøjgård (DKE) | Bornholm Energy Island (BEI) | DC | None | 229 | 525 | 1200 |  | VCS |  | 988 | 0 | 5.5 | +-20% | ++ | ++ | + (between sync areas)
1794 | Bornholm Energy Island: BEI-DE | 1106 | DC connection from mainland Germany (Stilow) to Bornholm including converters in Stilow and on Bornholm, as well as AC and MTDC components on the island of Bornholm | 12-2029 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | Stilow (DE) | Bornholm Energy Island (BEI) | DC | None | 193 | 525 | 2000 |  | VCS |  | 1091 | 0 | 5.5 | +-20% | ++ | ++ | + (between sync areas)
1792 | EuroAfrica Interconnector | 1107 | The EuroAfrica Interconnector consists of a 500 kV DC underwater electric cable and any essential equipment and/or installation for interconnecting the Cypriot and the Egyptian transmission networks (offshore). The Interconnector will have a total capacity of 2000 MW and a total length of 498km and allow for reverse transmission of electricity. | 12-2026 | 3 | TRUE | New Investment |  | OffshoreDCTransmissionCable | Kofinou | Damietta (Egypt) | DC | Bipolar | 512 | 500 | 1000 |  | VCS |  | 1036 | 0 | 13.7 | 10% | ++ | ++ | + (between sync areas)
1796 | New 400 kV overhead line between Aliano and Montecorvino | 1109 | New 400 kV overhead line between Aliano and Montecorvino | 12-2032 | 2 | TRUE | New Investment |  | ACTransmissionLine | Aliano | Montecorvino | AC | None | 116 | 400 | 0 | 1870 |  |  | 274 | 0 | 0.5 | 0% | ++ | ++ | 0 | 61 | Other |  | 1 | Other
1797 | New 400 kV overhead line in the northern area of Benevento | 1109 | New 400 kV overhead line in the northern area of Benevento | 12-2035 | 2 | FALSE | New Investment |  | ACTransmissionLine | Benevento | New Substation | AC | None | 42 | 400 | 0 | 1870 |  |  | 60 | 0 | 0.2 | 0% | ++ | ++ | 0 | 25 | Other |  | 1 | Other
1798 | New 400 kV submarine cable Bolano-Annunziata | 1110 | New 400 kV submarine cable Bolano-Annunziata | 12-2026 | 2 | TRUE | New Investment |  | ACTransmissionLine | Bolano | Annunziata | AC | None | 9 | 400 | 0 | 1040 |  |  | 175 | 0 | 0.25 | 0% | ++ | ++ | 0 | 2 | Other |  | 2 | Other
1799 | GRITA 2 | 1112 | New HVDC link between Italy (Galatina) and Greece (Arachthos) with an NTC increase of 500 MW. | 12-2031 | 1 | TRUE | New Investment |  | DCTransmissionLine | Galatina (IT) | Arachthos (GR) | DC | MonopolarBipolar | 320 | 400 | 500 |  | VCS |  | 750 | 0 | 0.75 | 10% | ++ | ++ | + (between sync areas) | 2 | Other | - | 2 | Other | -
1804 | Bisamberg (AT) - Wien SO (AT) - Parndorf (AT) | 1119 | Reinforcement/Upgrade 220-kV Overhead Line | 12-2031 | 1 | TRUE | New Investment |  | ACTransmissionLine | Bisamberg (AT) | Parndorf (AT) | AC | None | 85 | 380 | 0 |  |  |  | 280 | 0 | 0.8 | 10% | ++ | ++ | 0
1806 | Wien SO (AT) – Ternitz (AT) – Hessenberg (AT) | 1120 | Reinforcement/Upgrade 220-kV Overhead Line | 12-2033 | 1 | TRUE | New Investment |  | ACTransmissionLine | Wien SO (AT) | Hessenberg (AT) | AC | None | 156 | 220 | 0 |  |  |  | 230 | 0 | 0.7 | 10% | ++ | ++ | 0
1805 | Hessenberg (AT) - Weißenbach (AT) | 1121 | Reinforcement/Upgrade 220-kV Overheadline | 12-2029 | 2 | TRUE | New Investment |  | ACTransmissionLine | Hessenberg (AT) | Weißenbach (AT) | AC | None | 71 | 220 | 0 |  |  |  | 104 | 0 | 0.3 | 10% | ++ | ++ | 0
1810 | HVDC converter stations and cables | 1122 | HVDC offshore platform, onshore converter station, hvdc cables | 09-2031 | 1 | TRUE | New Investment |  | OffshoreSubstation | Centre Manche 1 | Menuel | DC | Monopolar | 100 | 320 | 1250 |  | VCS |  | 1350 | 0 | 0 | 30% | ++ | ++ | + (between sync areas)
1811 | Offshore Wind Connection Centre Manche 2 | 1123 | HVDC offshore platform + onshore station + HVDC onshore & offshore cables | 09-2032 | 1 | TRUE | New Investment |  | OffshoreSubstation | Centre Manche 2 | Tourbe | DC | Monopolar | 100 | 320 | 1250 |  | VCS |  | 1350 | 0 | 0 | 50% | ++ | ++ | + (between sync areas)
1812 | Offshore Wind Connection South Britanny | 1124 | HVAC offshore platform + onshore and offshore cables + onshore substation | 11-2029 | 1 | TRUE | New Investment |  | OffshoreSubstation | Bretagne Sud | tbd | AC | None | 70 | 225 | 0 |  |  |  | 750 | 0 | 0 | 30% | ++ | ++ | 0
1808 | AO6 Occitanie | 1125 | HVAC 225 kV offshore connection | 09-2030 | 1 | TRUE | New Investment |  | OffshoreACTransmissionCable | Tbd | Tbd | AC | None | 70 | 225 | 0 |  |  |  | 650 | 0 | 0 | 50%
1809 | AO6 Occitanie | 1126 | HVAC 225 kV offshore connection | 09-2030 | 1 | TRUE | New Investment |  | OffshoreACTransmissionCable | Tbd | Tbd | AC | None | 70 | 225 | 0 |  |  |  | 650 | 0 | 0 | 50% | ++ | ++ | 0
1813 | Offshore wind connection South Atlantic | 1127 | High voltage wind farm connection between 500 MW and 2 GW, including ˜100 km of underground cables, 2 substations (offshore and inland) and reactive compensation substation or converting HVDC/HVAC substation. Ongoing public debate to define the location of the offshore wind farm and its production capacity. Therefore the characteristics of the electrical connection are not defined yet. | 12-2030 | 1 | TRUE | New Investment |  | OffshoreDCTransmissionCable | TBD | TBD | DC | None | 0 | 0 | 0 |  | VCS |  | 1350 | 0 | 0 | 0% | ++ | ++ | + (between sync areas)
2 | Pedralva-Sobrado | 1129 | New double circuit Pedralva (PT) - Sobrado (PT) 400kV OHL, (only one circuit installed in a first step). | 12-2029 | 2 | TRUE | Rescheduled | Due to increasing difficulties in the identification of feasible corridors with acceptable environmental and social impact, it was decided to reassess the project and its configuration considering the new network developments in the region and the update on the expected generation and demand evolution. | ACTransmissionLine | Pedralva (PT) | Sobrado (PT) | AC | None | 67 | 400 | 0 | 1631 |  |  | 29.1 | 0 | 0.068 | ±10%% | ++ | ++ | 0

## Stor.Projects
TYNDP 2022 - General description of storage projects | [17 empty] | Needs addressed by the project |  |  |  | Projects costs |  |  |  | Technical characteristics of the project |  |  |  |  | Residual impact of the project |  |  | CBA
Project ID | Project Name | Promoters | Country | National development plan(s) | Storage technology | Project description | Commissioning year estimated by the promoter(s) | Status ID 1 : Under Consideration 2 : In Planning but not permitting 3 : In permitting 4 : Under Construction | Progress of the project since TYNDP2020 | Explanation in case of delay | Type of project - Is it an upgrade of existing infrastructure? | Is the project on the 5th PCI list? | PCI number | Inclusion in previous TYNDPs | Is the project in the reference grid 2027? | Is the project in the reference grid 2035? | Where can one find more information on the project? (ex: project website url) | Needs addressed by the project | Explanation by the promoter on how the project addresses the system needs | Relevant system needs study results in 2030 | Relevant system needs study results in 2040 | Estimated CAPEX (MEUR) | Sustaining CAPEX (Meuro) | Estimated OPEX (MEUR/year) | Cost Uncertainty Range | Total turbining capacity (MW) | Storage Capacity (GWh) | Total Pumping Capacity of Pump Storage (MW) | Roundtrip efficiency (%) | Operational lifetime (Years) | Residual Environmental Impact | Residual Social Impact | Other Residual Impact | Comments on CBA results by the project promoter

## 2030NT
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_network | ΔCO2_market_SEW |  |  | ΔCO2_network_SEW |  |  | ΔRES |  |  | ΔRES_MW | ΔNOx | ΔNH3 | ΔSO2 | ΔPM5 | ΔPM10 | ΔNMVOC | Δlosses | Δlosses_monetized | ΔSoS |  |  | ΔSoS_monetized
|  |  | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | low | mid | high | low | mid | high | weighted avg | max | min | Explicit | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | max | min | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW | ton / year | ton / year | ton / year | ton / year | ton / year | ton / year | GWh / year | M€ / year | MWh / year | MWh / year | MWh / year | M€ / year | M€ / year | M€ / year
1 | RES in north of Portugal | TOOT | 40 | 43 | 34 | 13 | 16 | 11 | 29 | 39 | 17 | -192 | -160 | -233 | 10 | 0 | 6 | 23 | 0 | 0 | 1 | 516 | 680 | 306 | 1154 | -190 | -18 | -68 | -12 | -7 | -6 | 12 | 1 | 0 | 0 | 0 | 0 | 0 | 0
4 | Interconnection Portugal-Spain | TOOT | 11 | 15 | 4 | 4 | 7 | 1 | 7 | 10 | 2 | -64 | -7 | -102 | 5 | 0 | 2 | 8 | 0 | 0 | 1 | 120 | 184 | 38 | 0 | -116 | -6 | -83 | -7 | -4 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | Biscay Gulf | TOOT | 268 | 293 | 240 | 111 | 123 | 98 | 114 | 126 | 103 | -1579 | -1398 | -1761 | 415 | 0 | 47 | 188 | 0 | 12 | 49 | 2023 | 2225 | 1790 | 0 | -1622 | -170 | -237 | -129 | -83 | -51 | 1748 | 77 | 1838 | 1838 | 1838 | 23 | 23 | 23
26 | Reschenpass Interconnector Project | TOOT | 16 | 20 | 14 | 14 | 18 | 9 | 2 | 4 | 1 | -195 | -131 | -250 | 10 | 0 | 6 | 23 | 0 | 0 | 1 | 37 | 69 | 21 | 0 | -291 | -20 | -185 | -19 | -12 | -6 | 51 | 2 | 37 | 37 | 37 | 0 | 0 | 0
28 | Italy-Montenegro | PINT | 20 | 25 | 16 | 13 | 18 | 8 | 7 | 8 | 6 | -187 | -111 | -263 | 33 | 0 | 6 | 22 | 0 | 1 | 4 | 126 | 147 | 106 | 0 | -145 | -13 | -65 | -11 | -8 | -4 | 83 | 6 | 0 | 0 | 0 | 0 | 0 | 0
29 | Italy-Tunisia | TOOT | 59 | 65 | 52 | 22 | 23 | 22 | 9 | 11 | 7 | -318 | -314 | -323 | 17 | 0 | 10 | 38 | 0 | 1 | 2 | 168 | 208 | 129 | 0 | -305 | -36 | 8 | -25 | -15 | -11 | -16 | 2 | 974 | 974 | 974 | 9.741186 | 9.741186 | 9.741186
33 | Central Northern Italy | TOOT | 3 | 4 | 3 | 2 | 3 | 2 | 3 | 3 | 2 | -35 | -33 | -36 | 29 | 0 | 1 | 4 | 0 | 1 | 4 | 50 | 63 | 38 | 0 | -23 | 0 | -32 | -1 | -1 | 0 | 56 | 5 | 33 | 33 | 33 | 0 | 0 | 0
35 | CZ Southwest-east corridor | PINT | 50 | 53 | 47 | 27 | 30 | 23 | 15 | 20 | 12 | -382 | -322 | -427 | 64 | 0 | 11 | 46 | 0 | 2 | 8 | 267 | 379 | 202 | 0 | -418 | -53 | 46 | -36 | -23 | -16 | 340 | 12 | 169 | 169 | 169 | 0 | 0 | 0
40 | Belgium-Luxembourg-Germany: long-term perspective | light PINT | 13 | 16 | 12 | 7 | 8 | 5 | 5 | 8 | 2 | -98 | -76 | -110 | N/A | 0 | 3 | 12 | N/A | N/A | N/A | 84 | 143 | 38 | 0 | -118 | -11 | -12 | -13 | -9 | -3 | N/A | N/A | 107 | 107 | 107 | 1.4296 | 1.4296 | 1.4296
47 | Westtirol (AT) - Vöhringen (DE) | PINT | 43 | 45 | 42 | 18 | 20 | 16 | 15 | 22 | 11 | -259 | -229 | -281 | 48 | 0 | 8 | 31 | 0 | 1 | 6 | 261 | 402 | 186 | 0 | -342 | -27 | -149 | -27 | -18 | -8 | 312 | 10 | 197 | 197 | 197 | 0 | 0 | 0
81 | North South Interconnector | TOOT | 87 | 92 | 82 | 30 | 39 | 20 | 35 | 55 | 17 | -430 | -281 | -561 | 19 | 0 | 13 | 51 | 0 | 1 | 2 | 620 | 975 | 317 | 0 | -396 | -51 | 34 | -30 | -18 | -15 | 104 | 3 | 152 | 152 | 152 | 1.52448 | 1.52448 | 1.52448
85 | Integration of RES in Alentejo | TOOT | 26 | 35 | 17 | 6 | 7 | 2 | 34 | 43 | 29 | -81 | -32 | -102 | 43 | 0 | 2 | 10 | 0 | 1 | 5 | 611 | 757 | 541 | 442 | -94 | -6 | -101 | -2 | -1 | -2 | 223 | 8 | 0 | 0 | 0 | 0 | 0 | 0
94 | GerPol Improvements | TOOT | 107 | 109 | 106 | 119 | 125 | 114 | 17 | 22 | 9 | -1707 | -1623 | -1781 | N/A | 0 | 51 | 203 | N/A | N/A | N/A | 311 | 387 | 161 | 0 | -3247 | -3 | -4621 | -182 | -123 | -2 | N/A | N/A | 816 | 816 | 816 | 9.07438 | 9.07438 | 9.07438
103 | Reinforcements Ring NL phase I | TOOT | 11 | 12 | 9 | 5 | 7 | 4 | 3 | 5 | 2 | -75 | -57 | -93 | -14 | 0 | 2 | 9 | 0 | 0 | -2 | 58 | 80 | 35 | 0 | -44 | -9 | 22 | -2 | -1 | -3 | -85 | -3 | 49 | 49 | 49 | 0.65642 | 0.65642 | 0.65642
107 | Celtic Interconnector | TOOT | 131 | 135 | 128 | 41 | 47 | 32 | 104 | 110 | 101 | -590 | -460 | -678 | 164 | 0 | 18 | 70 | 0 | 5 | 19 | 1866 | 1944 | 1785 | 0 | -585 | -55 | -144 | -45 | -28 | -16 | 712 | 29 | 892 | 892 | 892 | 10 | 10 | 10
111 | Aurora line (3rd AC Finland-Sweden north) | TOOT | 46 | 47 | 46 | 17 | 18 | 16 | 4 | 4 | 4 | -240 | -224 | -256 | 42 | 0 | 7 | 29 | 0 | 1 | 5 | 76 | 77 | 74 | 0 | -804 | -15 | -2218 | -36 | -61 | -6 | 162 | 7 | 634 | 634 | 634 | 6.020514 | 6.020514 | 6.020514
120 | Belgian Modular Offshore Grid II (MOG II) | TOOT | 634 | 634 | 634 | 162 | 162 | 162 | 789 | 789 | 789 | -2321 | -2321 | -2321 | 6 | 0 | 70 | 276 | 0 | 0 | 1 | 13531 | 13531 | 13531 | 3500 | -2319 | -188 | -1169 | -158 | -102 | -58 | 826 | 40 | 0 | 0 | 0 | 0 | 0 | 0
121 | Nautilus: multi-purpose interconnector Belgium - UK | PINT | 144 | 163 | 130 | 53 | 61 | 47 | 62 | 63 | 60 | -753 | -677 | -874 | 110 | 0 | 23 | 90 | 0 | 3 | 13 | 1086 | 1121 | 1051 | 0 | -1027 | -84 | -633 | -74 | -64 | -26 | 359 | 21 | 242 | 242 | 242 | 3.107832 | 3.107832 | 3.107832
123 | LitPol Link Stage 2 | TOOT | 178 | 179 | 177 | 161 | 161 | 161 | 17 | 18 | 16 | -2301 | -2295 | -2307 | -16 | 0 | 69 | 274 | 0 | 0 | 0 | 295 | 309 | 282 | 0 | 2349 | 22 | 5601 | 140 | 178 | 8 | -36 | -3 | 3039 | 3039 | 3039 | 21 | 21 | 21
124 | NordBalt phase 2 | PINT | 28 | 32 | 24 | 21 | 23 | 18 | 5 | 7 | 4 | -301 | -256 | -328 | -22 | 0 | 9 | 36 | 0 | -1 | -1 | 88 | 124 | 67 | 0 | -406 | -13 | -2904 | -36 | -108 | -4 | -120 | -4 | 109 | 109 | 109 | 1.130793 | 1.130793 | 1.130793
126 | SE North-south short-term reinforcements | TOOT | 50 | 51 | 49 | 28 | 33 | 19 | 4 | 5 | 4 | -394 | -277 | -470 | 23 | 0 | 12 | 47 | 0 | 1 | 3 | 78 | 82 | 75 | 0 | -796 | -36 | -1060 | -45 | -39 | -12 | 147 | 5 | 913 | 913 | 913 | 0 | 0 | 0
127 | Central Southern Italy | TOOT | 6 | 8 | 5 | 1 | 2 | -1 | 3 | 4 | 2 | -12 | 11 | -28 | 46 | 0 | 0 | 1 | 0 | 1 | 6 | 49 | 67 | 28 | 0 | -65 | -2 | -101 | 0 | 0 | -1 | 123 | 8 | 0 | 0 | 0 | 0 | 0 | 0
130 | HVDC SuedOstLink Wolmirstedt to area Isar | TOOT | 245 | 245 | 245 | 12 | 12 | 12 | 69 | 69 | 69 | -421 | -421 | -421 | -8 | 0 | 13 | 50 | 0 | 0 | -1 | 686 | 686 | 686 | 0 | -691 | -691 | -731 | -44 | -29 | -6 | 230 | -3 | 0 | 0 | 0 | 0 | 0 | 0
132 | HVDC Line A-North | TOOT | 901 | 901 | 901 | 42 | 42 | 42 | 285 | 285 | 285 | -1503 | -1503 | -1503 | -118 | 0 | 45 | 179 | 0 | -4 | -14 | 2846 | 2846 | 2846 | 0 | -2419 | -2419 | -2558 | -150 | -99 | -23 | 588 | -23 | 0 | 0 | 0 | 0 | 0 | 0
138 | Black Sea Corridor | TOOT | 9 | 15 | 5 | 6 | 8 | 4 | 1 | 1 | 0 | -90 | -55 | -116 | N/A | 0 | 3 | 11 | N/A | N/A | N/A | 12 | 21 | 4 | 0 | -97 | -8 | -39 | -6 | -4 | -2 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
142 | CSE4 | TOOT | 2 | 4 | 1 | 2 | 3 | 0 | 0 | 0 | 0 | -23 | -5 | -40 | N/A | 0 | 1 | 3 | N/A | N/A | N/A | 3 | 6 | -4 | 0 | -52 | 7 | -145 | -1 | -1 | 2 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
144 | Mid Continental East corridor | TOOT | 15 | 15 | 14 | 11 | 14 | 10 | 1 | 2 | 0 | -162 | -139 | -198 | -11 | 0 | 5 | 19 | 0 | 0 | -1 | 22 | 37 | 7 | 0 | -178 | -12 | -130 | -9 | -6 | -4 | -57 | -2 | 91 | 91 | 91 | 1 | 1 | 1
150 | Italy-Slovenia | light PINT | 17 | 21 | 15 | 16 | 21 | 11 | 2 | 4 | 0 | -227 | -158 | -302 | 71 | 0 | 7 | 27 | 0 | 2 | 8 | 41 | 72 | 0 | 0 | -197 | -13 | -135 | -14 | -10 | -4 | 220 | 13 | 0 | 0 | 0 | 0 | 0 | 0
153 | France-Alderney-Britain | PINT | 172 | 176 | 169 | 53 | 54 | 51 | 143 | 148 | 133 | -754 | -733 | -765 | 173 | 0 | 23 | 90 | 0 | 5 | 21 | 2553 | 2713 | 2316 | 0 | -660 | -48 | -401 | -46 | -31 | -14 | 847 | 35 | 523 | 523 | 523 | 6 | 6 | 6
170 | Baltic States Synchronization with Continental Europe | TOOT | 236 | 260 | 203 | 219 | 230 | 203 | 33 | 49 | 21 | -3127 | -2904 | -3285 | 1 | 0 | 94 | 372 | 0 | 0 | 0 | 604 | 904 | 367 | 0 | 970 | 2 | 4471 | 58 | 142 | 2 | 97 | 1 | 3075 | 3075 | 3075 | 29.4 | 29.4 | 29.4
174 | Greenconnector | PINT | 38 | 44 | 32 | 40 | 41 | 39 | 2 | 4 | 1 | -568 | -555 | -581 | 178 | 0 | 17 | 68 | 0 | 5 | 21 | 31 | 75 | 7 | 0 | -622 | -54 | -240 | -48 | -31 | -16 | 252 | 19 | 0 | 0 | 0 | 0 | 0 | 0
176 | Hansa PowerBridge I | TOOT | 162 | 162 | 161 | 79 | 79 | 79 | 10 | 11 | 10 | -1130 | -1126 | -1135 | N/A | 0 | 34 | 135 | N/A | N/A | N/A | 181 | 190 | 171 | 0 | -1220 | -98 | -360 | -87 | -49 | -30 | N/A | N/A | 136 | 136 | 136 | 1.6399 | 1.6399 | 1.6399
183 | DKW-DE, Westcoast | TOOT | 61 | 67 | 50 | 29 | 36 | 18 | 11 | 18 | 3 | -420 | -259 | -521 | N/A | 0 | 13 | 50 | N/A | N/A | N/A | 191 | 317 | 59 | 0 | -256 | -48 | 291 | -30 | -18 | -14 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
186 | East of Austria | TOOT | 290 | 296 | 287 | 94 | 99 | 87 | 272 | 273 | 270 | -1316 | -1247 | -1352 | -18 | 0 | 40 | 159 | 0 | -1 | -2 | 4968 | 5099 | 4819 | 2000 | -1461 | -131 | -534 | -109 | -70 | -40 | -44 | -3 | 0 | 0 | 0 | 0 | 0 | 0
187 | St. Peter (AT) - Pleinting (DE) | PINT | 99 | 106 | 95 | 39 | 44 | 32 | 31 | 34 | 29 | -553 | -455 | -623 | 116 | 0 | 17 | 66 | 0 | 3 | 14 | 546 | 588 | 495 | 0 | -762 | -60 | -315 | -62 | -40 | -18 | 754 | 24 | 375 | 375 | 375 | 4.15968 | 4.15968 | 4.15968
190 | NorthConnect | TOOT | 269 | 306 | 238 | 108 | 119 | 94 | 147 | 153 | 142 | -1546 | -1339 | -1705 | 26 | 0 | 46 | 184 | 0 | 1 | 3 | 2561 | 2625 | 2473 | 0 | -1361 | -125 | -430 | -102 | -64 | -38 | 282 | 7 | 587 | 587 | 587 | 6.413366 | 6.413366 | 6.413366
200 | CZ Northwest-South corridor | TOOT | 58 | 64 | 55 | 33 | 36 | 30 | 16 | 20 | 13 | -474 | -434 | -516 | 39 | 0 | 14 | 56 | 0 | 1 | 5 | 291 | 355 | 218 | 0 | 5180 | 8 | 7622 | 294 | 210 | 5 | 278 | 8 | 241 | 241 | 241 | 3 | 3 | 3
210 | Würmlach (AT) - Somplago (IT) interconnection | TOOT | 8 | 12 | 7 | 8 | 10 | 7 | 2 | 8 | 0 | -119 | -98 | -140 | 4 | 0 | 4 | 14 | 0 | 0 | 0 | 39 | 132 | 3 | 0 | -150 | -3 | -92 | -12 | -6 | -1 | 5 | 0 | 17 | 17 | 17 | 0 | 0 | 0
219 | EuroAsia Interconnector | TOOT | 61 | 80 | 42 | 17 | 25 | 9 | 9 | 11 | 7 | -247 | -135 | -360 | 270 | 0 | 7 | 29 | 0 | 8 | 32 | 157 | 184 | 130 | 0 | 5992 | -5 | 8602 | 364 | 256 | -1 | 860 | 50 | 2783 | 2783 | 2783 | 28 | 28 | 28
225 | 2nd interconnector Belgium - Germany | light PINT | 26 | 34 | 22 | 11 | 12 | 9 | 11 | 14 | 7 | -159 | -125 | -173 | N/A | 0 | 5 | 19 | N/A | N/A | N/A | 196 | 247 | 127 | 0 | -174 | -21 | -7 | -14 | -10 | -6 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
227 | Transbalkan Corridor | TOOT | 0 | 1 | 0 | 0 | 2 | -1 | 0 | 0 | 0 | -5 | 12 | -31 | 14 | 0 | 0 | 1 | 0 | 0 | 2 | 2 | 6 | -2 | 0 | -42 | 3 | -107 | 0 | 0 | 1 | 23 | 2 | 0 | 0 | 0 | 0 | 0 | 0
228 | Muhlbach - Eichstetten | TOOT | 22 | 24 | 18 | 11 | 13 | 9 | 9 | 12 | 6 | -158 | -129 | -181 | 40 | 0 | 5 | 19 | 0 | 1 | 5 | 159 | 205 | 112 | 0 | -315 | -12 | -302 | -19 | -12 | -4 | 192 | 7 | 199 | 199 | 199 | 2 | 2 | 2
230 | GerPol Power Bridge I | TOOT | 322 | 334 | 311 | 405 | 421 | 385 | 34 | 35 | 33 | -5784 | -5498 | -6017 | N/A | 0 | 174 | 688 | N/A | N/A | N/A | 592 | 611 | 573 | 0 | -4187 | 58 | -5867 | -255 | -156 | 18 | N/A | N/A | 411 | 411 | 411 | 4.409354 | 4.409354 | 4.409354
231 | Beznau - Tiengen | PINT | 42 | 46 | 37 | 15 | 18 | 11 | 20 | 25 | 13 | -208 | -156 | -252 | N/A | 0 | 6 | 25 | N/A | N/A | N/A | 350 | 460 | 230 | 0 | -261 | -30 | -5 | -22 | -14 | -9 | N/A | N/A | 49 | 49 | 49 | 1 | 1 | 1
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Bergrheinfeld West | TOOT | 2032 | 2032 | 2032 | 88 | 88 | 88 | 652 | 652 | 652 | -3160 | -3160 | -3160 | -167 | 0 | 95 | 376 | 0 | -5 | -20 | 6516 | 6516 | 6516 | 0 | -4554 | -4554 | -3974 | -310 | -203 | -59 | 970 | -35 | 0 | 0 | 0 | 0 | 0 | 0
239 | Fenno-Skan 1 renewal | light PINT | 12 | 13 | 11 | 4 | 5 | 3 | 4 | 9 | 0 | -54 | -40 | -78 | N/A | 0 | 2 | 6 | N/A | N/A | N/A | 70 | 170 | 5 | 0 | -111 | -7 | -341 | -6 | -12 | -2 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
243 | New 400 kV interconnection line between Serbia and Croatia | light PINT | 8 | 11 | 5 | 8 | 17 | 1 | 2 | 3 | 1 | -111 | -17 | -238 | N/A | 0 | 3 | 13 | N/A | N/A | N/A | 29 | 46 | 11 | 0 | -86 | -12 | 25 | -10 | -7 | -3 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
244 | Vigy - Uchtelfangen area | PINT | 101 | 103 | 98 | 51 | 58 | 47 | 46 | 58 | 33 | -723 | -678 | -823 | 251 | 0 | 22 | 86 | 0 | 8 | 30 | 819 | 1071 | 570 | 0 | -1154 | -55 | -974 | -79 | -53 | -16 | 1132 | 45 | 703 | 703 | 703 | 8 | 8 | 8
247 | AQUIND Interconnector | PINT | 245 | 254 | 238 | 78 | 85 | 74 | 201 | 212 | 189 | -1116 | -1052 | -1221 | 199 | 0 | 33 | 133 | 0 | 6 | 24 | 3582 | 3928 | 3299 | 0 | -858 | -68 | -456 | -59 | -38 | -21 | 810 | 38 | 644 | 644 | 644 | 8 | 8 | 8
250 | Merchant line Castasegna (CH) - Mese (IT) | PINT | 8 | 14 | 2 | 6 | 9 | 0 | 1 | 2 | 0 | -92 | 5 | -134 | 0 | 0 | 3 | 11 | 0 | 0 | 0 | 13 | 37 | 0 | 0 | -139 | -16 | 15 | -14 | -10 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252 | Internal Belgian Backbone Center-East: HTLS upgrade Massenhoven-VanEyck-Gramme-Courcelles-Bruegel-Mercator | PINT | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -10 | 0 | 0 | 2 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -35 | -2 | 0 | 0 | 0 | 0 | 0 | 0
253 | Upstream reinforcement in France to increase FR-CH capacity | PINT | 18 | 23 | 14 | 10 | 16 | 6 | 1 | 2 | 0 | -147 | -87 | -224 | 154 | 0 | 4 | 18 | 0 | 5 | 18 | 27 | 42 | 1 | 0 | -155 | -22 | 73 | -17 | -11 | -6 | 792 | 31 | 304 | 304 | 304 | 4 | 4 | 4
254 | HVDC Ultranet Osterath to Philippsburg | TOOT | 90 | 90 | 90 | 5 | 5 | 5 | 27 | 27 | 27 | -196 | -196 | -196 | 203 | 0 | 6 | 23 | 0 | 6 | 24 | 275 | 275 | 275 | 0 | -322 | -322 | -259 | -30 | -20 | -2 | -394 | 30 | 0 | 0 | 0 | 0 | 0 | 0
259 | HU-RO | PINT | 8 | 9 | 8 | 5 | 6 | 4 | 1 | 2 | 0 | -68 | -52 | -83 | 142 | 0 | 2 | 8 | 0 | 4 | 17 | 11 | 31 | 2 | 0 | -6313 | -49 | -8396 | -400 | -280 | -15 | 362 | 23 | 161 | 161 | 161 | 0 | 0 | 0
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | PINT | 115 | 120 | 108 | 50 | 57 | 45 | 43 | 46 | 40 | -709 | -640 | -810 | 227 | 0 | 21 | 84 | 0 | 7 | 27 | 760 | 819 | 701 | 2000 | -944 | -74 | -611 | -66 | -56 | -23 | 776 | 38 | 152 | 152 | 152 | 1.45492 | 1.45492 | 1.45492
263 | Lake Constance East | light PINT | 92 | 97 | 88 | 40 | 48 | 29 | 34 | 43 | 29 | -569 | -414 | -684 | N/A | 0 | 17 | 68 | N/A | N/A | N/A | 609 | 792 | 508 | 0 | -896 | -57 | -542 | -68 | -44 | -17 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
267 | Hansa PowerBridge II | light PINT | 144 | 146 | 142 | 69 | 70 | 68 | 7 | 8 | 7 | -985 | -976 | -994 | N/A | 0 | 30 | 117 | N/A | N/A | N/A | 126 | 129 | 122 | 0 | -1074 | -95 | 47 | -80 | -37 | -29 | N/A | N/A | 103 | 103 | 103 | 0 | 0 | 0
270 | FR-ES project -Aragón-Atlantic Pyrenees | PINT | 132 | 148 | 107 | 52 | 60 | 45 | 56 | 62 | 48 | -750 | -647 | -860 | 372 | 0 | 22 | 89 | 0 | 11 | 44 | 1006 | 1137 | 857 | 0 | -799 | -83 | -116 | -66 | -42 | -25 | 1503 | 71 | 791 | 791 | 791 | 10 | 10 | 10
276 | FR-ES project -Navarra-Landes | PINT | 132 | 148 | 107 | 52 | 60 | 45 | 56 | 62 | 48 | -750 | -647 | -860 | 372 | 0 | 22 | 89 | 0 | 11 | 44 | 1006 | 1137 | 857 | 0 | -799 | -83 | -116 | -66 | -42 | -25 | 1502 | 71 | 791 | 791 | 791 | 10 | 10 | 10
280 | FR-BE: study Lonny-Achene-Gramme | PINT | 44 | 46 | 43 | 27 | 30 | 21 | 19 | 23 | 14 | -383 | -305 | -431 | 119 | 0 | 11 | 46 | 0 | 4 | 14 | 334 | 422 | 251 | 0 | -577 | -29 | -467 | -40 | -26 | -9 | 465 | 21 | 299 | 299 | 299 | 3 | 3 | 3
283 | TuNur Italy | PINT | 813 | 856 | 776 | 279 | 297 | 263 | 730 | 732 | 729 | -3981 | -3756 | -4248 | 98 | 0 | 119 | 474 | 0 | 3 | 12 | 12650 | 12817 | 12458 | 4900 | -3706 | -426 | -168 | -297 | -189 | -128 | 742 | 19 | 0 | 0 | 0 | 0 | 0 | 0
285 | GridLink | PINT | 172 | 176 | 169 | 53 | 54 | 51 | 143 | 148 | 133 | -754 | -733 | -765 | 222 | 0 | 23 | 90 | 0 | 7 | 26 | 2553 | 2713 | 2316 | 0 | -660 | -48 | -401 | -46 | -31 | -14 | 898 | 42 | 523 | 523 | 523 | 6 | 6 | 6
286 | Greenlink | PINT | 54 | 57 | 52 | 23 | 29 | 19 | 33 | 35 | 31 | -330 | -278 | -417 | 26 | 0 | 10 | 39 | 0 | 1 | 3 | 584 | 614 | 543 | 0 | -67418 | -5059 | -42593 | -4778 | -3518 | -1539 | 118 | 4 | 503 | 503 | 503 | 5.183647 | 5.183647 | 5.183647
293 | Southern Aegean Interconnector | PINT | 85 | 89 | 79 | 28 | 32 | 26 | 76 | 80 | 74 | -406 | -364 | -457 | 83 | 0 | 12 | 48 | 0 | 2 | 10 | 1356 | 1373 | 1331 | 582 | -5926 | -100 | -7305 | -379 | -264 | -31 | 193 | 12 | 0 | 0 | 0 | 0 | 0 | 0
297 | BRABO II + III | TOOT | 19 | 21 | 16 | 3 | 4 | 2 | 19 | 23 | 14 | -40 | -22 | -63 | 93 | 0 | 1 | 5 | 0 | 3 | 11 | 340 | 412 | 239 | 0 | -138 | -4 | -152 | -7 | -4 | -1 | 390 | 17 | 292 | 292 | 292 | 3.73546 | 3.73546 | 3.73546
299 | SACOI3 | TOOT | 112 | 118 | 107 | 31 | 34 | 28 | 4 | 6 | 3 | -439 | -393 | -489 | 36 | 0 | 13 | 52 | 0 | 1 | 4 | 69 | 112 | 46 | 0 | -1018 | 18 | -2684 | -8 | -156 | -1 | 116 | 6 | 958 | 958 | 958 | 8 | 8 | 8
309 | NeuConnect | TOOT | 213 | 228 | 198 | 84 | 85 | 82 | 124 | 130 | 118 | -1197 | -1172 | -1211 | 187 | 0 | 36 | 142 | 0 | 6 | 22 | 2220 | 2307 | 2167 | 0 | -1150 | -94 | -475 | -85 | -54 | -28 | 719 | 33 | 426 | 426 | 426 | 5.018173 | 5.018173 | 5.018173
312 | St. Peter (AT) - Tauern (AT) | TOOT | 175 | 183 | 165 | 64 | 70 | 59 | 65 | 77 | 53 | -1135 | -850 | -1444 | 127 | 0 | 28 | 110 | 0 | 4 | 15 | 1166 | 1367 | 928 | 0 | -1930 | -125 | -1119 | -145 | -92 | -37 | 958 | 26 | 1495 | 1495 | 1495 | 17 | 17 | 17
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | TOOT | 180 | 183 | 176 | 80 | 88 | 70 | 61 | 77 | 48 | -1143 | -994 | -1254 | 148 | 0 | 34 | 136 | 0 | 4 | 18 | 1094 | 1367 | 816 | 0 | -1487 | -114 | -676 | -112 | -71 | -34 | 1037 | 31 | 1495 | 1495 | 1495 | 17 | 17 | 17
323 | Dekani (SI) - Zaule (IT) interconnection | TOOT | 1 | 1 | 0 | 0 | 2 | -1 | 1 | 2 | 0 | -6 | 10 | -30 | -6 | 0 | 0 | 1 | 0 | 0 | -1 | 15 | 33 | 0 | 0 | -40 | 5 | -99 | -2 | -2 | 2 | -8 | -1 | 3 | 3 | 3 | 0 | 0 | 0
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | TOOT | 6 | 11 | 1 | 1 | 2 | -1 | 2 | 4 | 0 | -11 | 8 | -22 | -8 | 0 | 0 | 1 | 0 | 0 | -1 | 30 | 74 | 3 | 0 | -43 | 1 | -76 | -1 | 0 | 0 | -15 | -1 | 2 | 2 | 2 | 0 | 0 | 0
325 | Obersielach (AT) - Podlog (SI) | PINT | 23 | 30 | 17 | 21 | 28 | 15 | 3 | 6 | 2 | -296 | -208 | -398 | 53 | 0 | 9 | 35 | 0 | 2 | 6 | 54 | 105 | 30 | 0 | -339 | -35 | -87 | -27 | -18 | -10 | 156 | 9 | 0 | 0 | 0 | 0 | 0 | 0
328 | Interconnector DE-LUX | TOOT | 0 | 1 | 0 | -1 | 0 | -2 | 0 | 0 | 0 | 10 | 30 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 4 | 7 | 2 | 0 | 5 | 1 | 1 | 1 | 1 | 0 | N/A | N/A | 6 | 6 | 6 | 0 | 0 | 0
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | TOOT | 416 | 416 | 416 | 149 | 149 | 149 | 324 | 324 | 324 | -2134 | -2134 | -2134 | 8 | 0 | 64 | 254 | 0 | 0 | 1 | 5561 | 5561 | 5561 | 0 | -1942 | -226 | -54 | -156 | -99 | -68 | 38 | 1 | 0 | 0 | 0 | 0 | 0 | 0
330 | 4th 400kV CZ-SK interconnector | light PINT | 3 | 4 | 1 | 5 | 7 | 2 | 0 | 1 | 0 | -67 | -31 | -105 | N/A | 0 | 2 | 8 | N/A | N/A | N/A | 5 | 17 | 0 | 0 | -62 | 0 | -82 | -6 | -4 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
333 | PST Foretaille | PINT | 89 | 92 | 86 | 45 | 49 | 43 | 1 | 2 | 0 | -647 | -612 | -696 | 128 | 0 | 19 | 77 | 0 | 4 | 15 | 15 | 40 | 3 | 0 | -769 | -70 | -256 | -59 | -39 | -21 | 665 | 26 | 45 | 45 | 45 | 1 | 1 | 1
335 | North Sea Wind Power Hub | light PINT | 798 | 821 | 765 | 733 | 746 | 720 | 3132 | 3262 | 2959 | -10470 | -10285 | -10654 | N/A | 0 | 314 | 1246 | N/A | N/A | N/A | 55163 | 55920 | 54581 | 12000 | -10823 | -903 | -5010 | -770 | -501 | -274 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
338 | Adriatic HVDC link | PINT | 15 | 18 | 11 | 9 | 10 | 8 | 6 | 11 | 2 | -129 | -115 | -143 | -31 | 0 | 4 | 15 | 0 | -1 | -4 | 118 | 201 | 35 | 0 | -145 | -12 | -44 | -14 | -10 | -3 | -41 | -3 | 139 | 139 | 139 | 0 | 0 | 0
339 | Tyrrhenian link | PINT | 3 | 5 | 1 | -1 | 2 | -3 | 2 | 3 | 2 | 12 | 48 | -23 | 143 | 0 | 0 | 0 | 0 | 4 | 17 | 41 | 55 | 26 | 0 | -15 | -6 | 37 | -3 | -2 | -2 | -214 | 22 | 91 | 91 | 91 | 0.91 | 0.91 | 0.91
340 | Avelgem-Courcelles (Boucle du Hainaut): new corridor | TOOT | 203 | 203 | 203 | 73 | 73 | 73 | 146 | 146 | 146 | -1041 | -1041 | -1041 | -87 | 0 | 31 | 124 | 0 | -3 | -10 | 2509 | 2509 | 2509 | 0 | -920 | -107 | -25 | -74 | -47 | -32 | -375 | -17 | 0 | 0 | 0 | 0 | 0 | 0
341 | North CSE Corridor | PINT | 1 | 1 | 0 | 0 | 2 | -2 | 0 | 0 | 0 | -4 | 34 | -26 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 4 | 7 | 2 | 0 | -9 | -7 | 84 | -4 | -3 | -2 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
342 | Central Balkan Corridor | PINT | 3 | 6 | 0 | 2 | 6 | 0 | 0 | 1 | 0 | -31 | 4 | -92 | N/A | 0 | 1 | 4 | N/A | N/A | N/A | 7 | 17 | 0 | 0 | 17 | -3 | 69 | -1 | -1 | -1 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
343 | CSE1 New | PINT | 3 | 4 | 3 | 3 | 5 | 1 | 0 | 1 | 0 | -37 | -12 | -70 | N/A | 0 | 1 | 4 | N/A | N/A | N/A | 8 | 11 | 5 | 0 | -29 | -7 | 59 | -5 | -4 | -2 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
346 | ZuidWest380 NL Oost | PINT | 10 | 13 | 8 | 0 | 1 | -4 | 10 | 13 | 6 | 5 | 56 | -21 | -188 | 0 | 0 | 0 | 0 | -6 | -22 | 190 | 238 | 102 | 0 | -76 | -4 | -60 | -7 | -5 | -1 | -1723 | -40 | 129 | 129 | 129 | 1.62512 | 1.62512 | 1.62512
349 | MaresConnect | PINT | 75 | 78 | 73 | 33 | 39 | 28 | 47 | 52 | 42 | -467 | -403 | -564 | 65 | 0 | 14 | 56 | 0 | 2 | 8 | 838 | 908 | 779 | 0 | -505 | -42 | -210 | -40 | -29 | -13 | 254 | 11 | 626 | 626 | 626 | 6.466547 | 6.466547 | 6.466547
350 | South Balkan Corridor | TOOT | 4 | 9 | 1 | 1 | 4 | 0 | 0 | 1 | 0 | -16 | 5 | -51 | N/A | 0 | 0 | 2 | N/A | N/A | N/A | 3 | 14 | 0 | 0 | 19 | 2 | 9 | 2 | 2 | 1 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
375 | Lienz (AT) - Veneto region (IT) 220 kV | PINT | 21 | 30 | 16 | 17 | 22 | 13 | 2 | 4 | 1 | -249 | -180 | -314 | 32 | 0 | 7 | 30 | 0 | 1 | 4 | 40 | 77 | 12 | 0 | -347 | -35 | -90 | -26 | -17 | -10 | 144 | 6 | 47 | 47 | 47 | 0 | 0 | 0
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | light PINT | 1 | 4 | 0 | 3 | 8 | -1 | 0 | 1 | 0 | -40 | 12 | -117 | N/A | 0 | 1 | 5 | N/A | N/A | N/A | 5 | 12 | 0 | 0 | 46 | -3 | 81 | 2 | 1 | -1 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | PINT | 10 | 13 | 8 | 0 | 2 | -4 | 11 | 13 | 6 | 4 | 56 | -22 | 122 | 0 | 0 | 0 | 0 | 4 | 14 | 190 | 238 | 103 | 0 | -68 | -5 | -32 | -7 | -5 | -1 | 108 | 4 | 129 | 129 | 129 | 1.62512 | 1.62512 | 1.62512
378 | Transformer Gatica | TOOT | [12 empty] | N/A | 0 | 0 | 0 | N/A | N/A | N/A |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
379 | Uprate Gatica lines | TOOT | [12 empty] | N/A | 0 | 0 | 0 | N/A | N/A | N/A |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
1034 | HVDC corridor from Northern Germany to Western Germany | PINT | 876 | 876 | 876 | 34 | 34 | 34 | 267 | 267 | 267 | -1209 | -1209 | -1209 | -61 | 0 | 36 | 144 | 0 | 2 | 7 | 2665 | 2665 | 2665 | 0 | -1745 | -1745 | -1632 | -107 | -70 | -24 | -250 | 12 | 0 | 0 | 0 | 0 | 0 | 0
1039 | SE North-south long-term reinforcements | light PINT | 11 | 16 | 6 | 8 | 16 | 0 | 4 | 10 | 1 | -116 | -1 | -230 | N/A | 0 | 3 | 14 | N/A | N/A | N/A | 75 | 182 | 11 | 0 | -130 | -11 | -105 | -9 | -7 | -3 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
1040 | LirIC | PINT | 53 | 61 | 47 | 20 | 21 | 19 | 30 | 33 | 28 | -287 | -276 | -298 | 13 | 0 | 9 | 34 | 0 | 0 | 2 | 540 | 565 | 518 | 0 | -291 | -31 | -39 | -25 | -17 | -9 | 153 | 3 | 301 | 301 | 301 | 3.134254 | 3.134254 | 3.134254
1041 | GREGY Green Energy Interconnector | PINT | 89 | 93 | 82 | 17 | 21 | 13 | 1 | 3 | 0 | -247 | -188 | -306 | 466 | 0 | 7 | 29 | 0 | 14 | 55 | 19 | 53 | 0 | 0 | -88 | -26 | 161 | -9 | -5 | -8 | 1331 | 93 | 1 | 1 | 1 | 0 | 0 | 0
1042 | Offshore Wind LT 1 | PINT | 72 | 76 | 68 | 16 | 22 | 11 | 131 | 147 | 113 | -224 | -150 | -314 | -8 | 0 | 7 | 27 |  | 0 | 0 | 2301 | 2544 | 2056 | 700 | -165 | -9 | -829 | -14 | -32 | -3 | -153 | -3 | 30 | 30 | 30 | 0.30672 | 0.30672 | 0.30672
1046 | Finnish North-South reinforcement | PINT | 10 | 10 | 10 | 0 | 0 | 0 | 10 | 10 | 10 | -4 | -4 | -4 | -81 | 0 | 0 | 1 | 0 | -2 | -10 | 186 | 186 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -624 | -18 | 0 | 0 | 0 | 0 | 0 | 0
1047 | Emden-Eemshaven | light PINT | 15 | 18 | 14 | 9 | 10 | 8 | 4 | 5 | 3 | -125 | -114 | -140 | N/A | 0 | 4 | 15 | N/A | N/A | N/A | 76 | 100 | 43 | 0 | -43 | -17 | 150 | -8 | -5 | -5 | N/A | N/A | 31 | 31 | 31 | 0.39996 | 0.39996 | 0.39996
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | PINT | 47 | 51 | 37 | 21 | 28 | 11 | 1 | 2 | 0 | -294 | -160 | -406 | 848 | 0 | 9 | 35 | 0 | 25 | 101 | 12 | 31 | 0 | 0 | -165 | -8 | -122 | -11 | -5 | -2 | 2401 | 161 | N/A | N/A | N/A | N/A | N/A | N/A
1049 | Cronos Energy Ltd | PINT | 170 | 181 | 163 | 59 | 61 | 55 | 107 | 113 | 104 | -840 | -788 | -874 | 28 | 0 | 25 | 100 | 0 | 1 | 3 | 1921 | 2001 | 1809 | 0 | -840 | -75 | -342 | -59 | -38 | -23 | 274 | 15 | 278 | 278 | 278 | 0 | 0 | 0
1050 | Tarchon Energy Ltd | PINT | 186 | 187 | 184 | 73 | 79 | 68 | 107 | 111 | 103 | -1046 | -978 | -1133 | 104 | 0 | 31 | 124 | 0 | 3 | 12 | 1910 | 1978 | 1842 | 0 | -939 | -87 | -281 | -73 | -47 | -26 | 431 | 20 | 187 | 187 | 187 | 2.27204 | 2.27204 | 2.27204
1051 | Aminth Energy Ltd | PINT | 143 | 146 | 138 | 49 | 59 | 44 | 93 | 101 | 84 | -704 | -625 | -843 | 31 | 0 | 21 | 84 | 0 | 1 | 4 | 1663 | 1745 | 1546 | 0 | -804 | -50 | -654 | -48 | -32 | -16 | 113 | 5 | 189 | 189 | 189 | 2.01166 | 2.01166 | 2.01166
1052 | Lienz (AT) - Obersielach (AT) | PINT | 26 | 28 | 23 | 19 | 24 | 15 | 3 | 6 | 0 | -247 | -184 | -337 | 48 | 0 | 8 | 33 | 0 | 1 | 6 | 47 | 105 | 5 | 0 | -323 | -33 | -68 | -27 | -19 | -10 | 128 | 7 | 0 | 0 | 0 | 0 | 0 | 0
1054 | Westtirol (AT) - Zell/Ziller (AT) | PINT | 43 | 46 | 38 | 15 | 20 | 5 | 13 | 22 | 4 | -258 | -229 | -281 | 64 | 0 | 6 | 25 | 0 | 2 | 8 | 233 | 402 | 67 | 0 | -691 | -36 | -485 | -53 | -35 | -10 | 362 | 12 | 197 | 197 | 197 | 0 | 0 | 0
1055 | Interconnection of Crete to the Mainland System of Greece | TOOT | 90 | 92 | 88 | 17 | 28 | 7 | 7 | 8 | 4 | -242 | -100 | -401 | 149 | 0 | 7 | 29 | 0 | 4 | 18 | 116 | 141 | 78 | 0 | -257 | -40 | 115 | -21 | -13 | -12 | 381 | 26 | 0 | 0 | 0 | 0 | 0 | 0
1058 | HVDC Interconnector DE-CH | light PINT | 77 | 80 | 73 | 35 | 37 | 31 | 31 | 40 | 26 | -493 | -439 | -535 | N/A | 0 | 15 | 59 | N/A | N/A | N/A | 558 | 744 | 460 | 0 | -674 | -49 | -334 | -52 | -33 | -14 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
1059 | Southern Italy | PINT | 1 | 3 | 0 | -1 | 0 | -3 | 0 | 1 | 0 | 14 | 37 | -7 | -13 | 0 | 0 | 0 | 0 | 0 | -2 | 8 | 12 | 4 | 0 | 46 | -3 | 88 | 3 | 2 | -1 | -36 | -2 | 0 | 0 | 0 | 0 | 0 | 0
1066 | Bulgaria - Turkey | light PINT | 157 | 166 | 152 | 191 | 193 | 189 | 1 | 2 | 0 | -2734 | -2707 | -2762 | N/A | 0 | 82 | 325 | N/A | N/A | N/A | 17 | 30 | 0 | 0 | -6892 | 51 | -12407 | -180 | -121 | -2 | N/A | N/A | 260 | 260 | 260 | 3 | 3 | 3
1067 | New AC 400 kV interconnection line Greece - Turkey | light PINT | 89 | 92 | 87 | 100 | 111 | 92 | 0 | 1 | 0 | -1429 | -1309 | -1586 | N/A | 0 | 43 | 170 | N/A | N/A | N/A | 7 | 20 | -4 | 0 | -3908 | 29 | -6979 | -106 | -71 | -1 | N/A | N/A | 181 | 181 | 181 | 2 | 2 | 2
1068 | LaSGo Link | light PINT | 29 | 33 | 24 | 22 | 25 | 17 | 5 | 6 | 3 | -315 | -238 | -361 | -1 | 0 | 9 | 37 | 0 | 0 | 0 | 86 | 113 | 44 | 0 | -429 | -16 | -3121 | -39 | -117 | -5 | 34 | 0 | 68 | 68 | 68 | 0.707353 | 0.707353 | 0.707353
1074 | Pannonian Corridor | PINT | 9 | 15 | 6 | 6 | 9 | 3 | 1 | 1 | 0 | -80 | -43 | -125 | 120 | 0 | 2 | 10 | 0 | 4 | 14 | 16 | 26 | 7 | 0 | -43 | -12 | 84 | -7 | -5 | -3 | 281 | 19 | 117 | 117 | 117 | 0 | 0 | 0
1082 | Sea-Socket | light PINT | 101 | 102 | 100 | 32 | 38 | 29 | 113 | 118 | 109 | -461 | -412 | -539 | N/A | 0 | 14 | 55 | N/A | N/A | N/A | 2005 | 2045 | 1955 | 700 | -431 | -42 | -110 | -35 | -23 | -13 | N/A | N/A | 21 | 21 | 21 | 0 | 0 | 0
1085 | Malta-Italy Cable Link No.2 | PINT | 13 | 16 | 11 | 3 | 5 | 2 | 1 | 2 | 0 | -49 | -22 | -65 | 45 | 0 | 1 | 6 | 0 | 1 | 5 | 15 | 38 | 3 | 0 | -32 | -9 | 86 | -7 | -5 | -2 | 94 | 7 | 3 | 3 | 3 | 0.03 | 0.03 | 0.03
1086 | Estonia internal grid reinforcement to increase RES connection capability (RRF project) | PINT | 64 | 65 | 62 | 13 | 15 | 11 | 123 | 124 | 122 | -180 | -151 | -209 | -1 | 0 | 5 | 21 | 0 | 0 | 0 | 2123 | 2125 | 2120 | 700 | -170 | -8 | -1152 | -17 | -46 | -2 | -11 | 0 | 88 | 88 | 88 | 0.873409 | 0.873409 | 0.873409
1088 | Latvia and Estonia Hybrid Off-Shore interconnector | PINT | 22 | 31 | 13 | 24 | 31 | 16 | 206 | 217 | 184 | -344 | -224 | -437 | -5 | 0 | 10 | 41 | 0 | 0 | 0 | 3573 | 3766 | 3263 | 1000 | -291 | -11 | -1563 | -23 | -58 | -3 | -77 | -1 | 0 | 0 | 0 | 0 | 0 | 0
1092 | Triton Link: offshore hybrid HVDC interconnector Belgium – Denmark | PINT | 139 | 150 | 131 | 176 | 181 | 168 | 729 | 773 | 671 | -2521 | -2406 | -2591 | 17 | 0 | 76 | 300 | 0 | 1 | 2 | 12844 | 13248 | 12377 | 3000 | -2610 | -215 | -1308 | -184 | -122 | -65 | 898 | 43 | 0 | 0 | 0 | 0 | 0 | 0
1094 | Estlink 3 | light PINT | 26 | 26 | 25 | 29 | 32 | 25 | 1 | 3 | 0 | -410 | -360 | -450 | -8 | 0 | 12 | 49 |  | 0 | 0 | 23 | 55 | 0 | 0 | -360 | -10 | -4181 | -42 | -157 | -3 | -28 | -2 | 27 | 27 | 27 | 0 | 0 | 0
1095 | Aurora line 2 (4th AC Finland-Sweden north) | light PINT | 22 | 23 | 21 | 7 | 8 | 7 | 1 | 1 | 0 | -102 | -94 | -111 | N/A | 0 | 3 | 12 | N/A | N/A | N/A | 12 | 24 | 0 | 0 | -342 | -11 | -875 | -16 | -26 | -4 | N/A | N/A | 291 | 291 | 291 | 3.034801 | 3.034801 | 3.034801
1096 | Beznau - Mettlen | PINT | 49 | 54 | 46 | 17 | 22 | 14 | 20 | 29 | 16 | -246 | -198 | -312 | N/A | 0 | 7 | 29 | N/A | N/A | N/A | 351 | 530 | 269 | 0 | -210 | -33 | 108 | -22 | -14 | -10 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
1097 | Upgrade to Konti-Skan | PINT | 97 | 121 | 76 | 43 | 54 | 34 | 15 | 16 | 14 | -610 | -480 | -771 | 132 | 0 | 18 | 73 | 0 | 4 | 16 | 269 | 282 | 246 | 0 | -1082 | -72 | -649 | -73 | -45 | -22 | 466 | 24 | 104 | 104 | 104 | 1.12884 | 1.12884 | 1.12884
1098 | Offshore Wind LT 2 | PINT | 74 | 76 | 71 | 16 | 22 | 11 | 128 | 147 | 113 | -233 | -151 | -314 | -2 | 0 | 7 | 28 | 0 | 0 | 0 | 2272 | 2545 | 2060 | 700 | -172 | -8 | -839 | -14 | -33 | -3 | -84 | -1 | 30 | 30 | 30 | 0.30672 | 0.30672 | 0.30672
1100 | Reinforcement of the existing CZ-DE interconnector (Hradec - Röhrsdorf) on the CZ side | PINT | 53 | 61 | 45 | 29 | 33 | 25 | 16 | 20 | 11 | -421 | -364 | -468 | 93 | 0 | 13 | 50 | 0 | 3 | 11 | 297 | 372 | 188 | 0 | -403 | -52 | 41 | -34 | -22 | -15 | 404 | 16 | 0 | 0 | 0 | 0 | 0 | 0
1102 | Mettlen - Ulrichen | light PINT | 14 | 15 | 14 | 4 | 5 | 2 | 6 | 9 | 4 | -59 | -26 | -76 | N/A | 0 | 2 | 7 | N/A | N/A | N/A | 110 | 167 | 76 | 0 | -50 | -11 | 87 | -8 | -5 | -3 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
1103 | Bickigen - Chippis | PINT | 36 | 38 | 34 | 11 | 13 | 9 | 15 | 20 | 11 | -160 | -127 | -182 | N/A | 0 | 5 | 19 | N/A | N/A | N/A | 265 | 375 | 191 | 0 | -137 | -25 | 104 | -14 | -9 | -7 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
1104 | Niederstedem - Roost | PINT | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 1 | 0 | 5 | 19 | -5 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 5 | 13 | 1 | 0 | 18 | -3 | 60 | -1 | -1 | -1 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
1105 | Georgia-Romania Black Sea (submarine) interconnection cable project | PINT | 20 | 38 | 2 | 16 | 22 | 12 | 3 | 4 | 2 | -228 | -170 | -315 | 10 | 0 | 7 | 27 | 0 | 0 | 1 | 45 | 70 | 25 | 0 | 406 | 74 | -329 | 41 | 26 | 22 | 80 | 2 | 0 | 0 | 0 | 0 | 0 | 0
1106 | Bornholm Energy Island (BEI) | TOOT | 45 | 62 | 23 | 104 | 108 | 98 | 388 | 414 | 351 | -1483 | -1398 | -1545 | 114 | 0 | 44 | 176 | 0 | 3 |  | 6822 | 7097 | 6468 | 2000 | -2402 | -167 | -1857 | -164 | -143 | -51 | 438 | 21 | 0 | 0 | 0 | 0 | 0 | 0
1107 | EuroAfrica Interconnector | PINT | 53 | 55 | 52 | 13 | 14 | 12 | 1 | 2 | 0 | -181 | -172 | -197 | -19 | 0 | 5 | 22 | 0 | -1 | -2 | 20 | 29 | 3 | 0 | -214 | -14 | -77 | -17 | -9 | -4 | -65 | -4 | 0 | 0 | 0 | 0 | 0 | 0
1109 | Basilicata - Campania reinforcements | PINT | 4 | 6 | 2 | 1 | 2 | 0 | 1 | 2 | 1 | -20 | -4 | -36 | -20 | 0 | 1 | 2 | 0 | -1 | -2 | 20 | 30 | 10 | 0 | -10 | -1 | -25 | 0 | -1 | 0 | -46 | -3 | 0 | 0 | 0 | 0 | 0 | 0
1110 | Sicily - Calabria | PINT | 2 | 4 | 1 | -1 | 0 | -3 | 1 | 1 | 1 | 20 | 40 | 1 | 14 | 0 | 0 | 0 | 0 | 0 | 2 | 20 | 27 | 14 | 0 | 23 | -2 | 65 | -1 | -1 | -1 | 32 | 2 | 89 | 89 | 89 | 0.89 | 0.89 | 0.89
1112 | GRITA 2 | PINT | 19 | 26 | 15 | 9 | 10 | 8 | 5 | 8 | 3 | -128 | -114 | -142 | 14 | 0 | 4 | 15 | 0 | 0 | 2 | 89 | 147 | 48 | 0 | -140 | -14 | -37 | -13 | -9 | -4 | 37 | 2 | 0 | 0 | 0 | 0 | 0 | 0
1119 | Bisamberg (AT) - Wien SO (AT) - Parndorf (AT) | PINT | 330 | 330 | 330 | 114 | 114 | 114 | 339 | 339 | 339 | -1566 | -1566 | -1566 | -46 | 0 | 49 | 194 | 0 | -1 | -6 | 5973 | 5973 | 5973 | 3000 | 69 | 0 | 97 | 4 | 3 | 0 | -131 | -7 | 0 | 0 | 0 | 0 | 0 | 0
1120 | Wien SO (AT) – Ternitz (AT) – Hessenberg (AT) | PINT | 81 | 81 | 81 | 34 | 34 | 34 | 75 | 75 | 75 | -369 | -369 | -369 | -27 | 0 | 15 | 59 | 0 | -1 | -3 | 1323 | 1323 | 1323 | 750 | 105 | 2 | 120 | 7 | 5 | 1 | -66 | -5 | 0 | 0 | 0 | 0 | 0 | 0
1121 | Hessenberg (AT) - Weißenbach (AT) | PINT | 49 | 49 | 49 | 21 | 21 | 21 | 50 | 50 | 50 | -278 | -278 | -278 | -21 | 0 | 9 | 36 | 0 | -1 | -3 | 889 | 889 | 889 | 600 | 16 | 1 | 9 | 2 | 1 | 0 | -63 | -4 | 0 | 0 | 0 | 0 | 0 | 0
1122 | Offshore Wind connection Centre Manche 1 | TOOT | 180 | 186 | 169 | 37 | 41 | 33 | 253 | 255 | 251 | -523 | -477 | -579 | 109 | 0 | 16 | 62 | 0 | 3 | 13 | 4396 | 4452 | 4319 | 1050 | -493 | -49 | -127 | -36 | -23 | -15 | 497 | 22 | 126 | 126 | 126 | 2 | 2 | 2
1123 | Offshore Wind Connection Centre Manche 2 | PINT | 215 | 217 | 213 | 46 | 52 | 39 | 293 | 306 | 275 | -656 | -563 | -749 | 109 | 0 | 20 | 78 | 0 | 3 | 13 | 5225 | 5306 | 5070 | 1250 | -583 | -58 | -178 | -42 | -28 | -18 | 523 | 23 | 125 | 125 | 125 | 2 | 2 | 2
1124 | Offshore Wind Connection South Britanny | TOOT | 43 | 47 | 36 | 9 | 13 | 6 | 59 | 62 | 55 | -126 | -92 | -186 | 12 | 0 | 4 | 15 | 0 | 0 | 1 | 1054 | 1091 | 1014 | 250 | -124 | -7 | -89 | -7 | -4 | -2 | 53 | 2 | 48 | 48 | 48 | 1 | 1 | 1
1125 | Offshore Wind Connection Occitanie | TOOT | 47 | 50 | 41 | 8 | 12 | 3 | 59 | 60 | 57 | -119 | -44 | -173 | 0 | 0 | 4 | 14 | 0 | 0 | 0 | 1049 | 1065 | 1036 | 250 | -150 | -14 | -58 | -10 | -6 | -4 | -28 | 0 | 115 | 115 | 115 | 1 | 1 | 1
1126 | Offshore Wind Connection PACA | TOOT | 45 | 47 | 42 | 10 | 11 | 9 | 58 | 60 | 57 | -137 | -127 | -156 | -12 | 0 | 4 | 16 | 0 | 0 | -1 | 1040 | 1050 | 1033 | 250 | -142 | -12 | -89 | -7 | -4 | -4 | -98 | -3 | 121 | 121 | 121 | 1 | 1 | 1
1127 | Offshore Wind Connection South Atlantic | PINT | 192 | 195 | 190 | 42 | 45 | 40 | 267 | 276 | 259 | -607 | -567 | -639 | 97 | 0 | 18 | 72 | 0 | 3 | 12 | 4594 | 4600 | 4589 | 1250 | -601 | -58 | -151 | -48 | -31 | -17 | 391 | 18 | 229 | 229 | 229 | 3 | 3 | 3
1129 | New RES at Minho region | TOOT | 44 | 47 | 40 | 11 | 13 | 10 | 49 | 52 | 45 | -156 | -144 | -179 | 14 | 0 | 5 | 19 | 0 | 0 | 2 | 870 | 904 | 829 | 400 | -128 | -14 | -17 | -9 | -5 | -4 | 55 | 3 | 0 | 0 | 0 | 0 | 0 | 0

## 2030DE
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_market_SEW |  |  | ΔCO2_network | ΔCO2_network_SEW |  |  | ΔRES |  |  | ΔRES_MW | ΔNOx | ΔNH3 | ΔSO2 | ΔPM5 | ΔPM10 | ΔNMVOC | Δlosses | Δlosses_monetized | ΔSoS |  |  | ΔSoS_monetized
|  |  | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | low | mid | high | weighted avg | low | mid | high | weighted avg | max | min | Explicit | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | max | min | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | ktonnes / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW | ton / year | ton / year | ton / year | ton / year | ton / year | ton / year | GWh / year | M€ / year | MWh / year | MWh / year | MWh / year | M€ / year | M€ / year | M€ / year
1 | RES in north of Portugal | TOOT | 60 | 66 | 56 | 25 | 27 | 19 | 58 | 76 | 41 | -316 | -248 | -345 | 0 | 7 | 35 | 10 | 0 | 0 | 1 | 887 | 1030 | 739 | 1154 | -389 | -42 | -62 | -29 | -19 | -13 | 12 | 2 | 0 | 0 | 0 | 0 | 0 | 0
4 | Interconnection Portugal-Spain | TOOT | 19 | 29 | 11 | 4 | 8 | -1 | 18 | 26 | 13 | -50 | 18 | -106 | 0 | 1 | 6 | 3 | 0 | 0 | 0 | 306 | 464 | 213 | 0 | -126 | -19 | 62 | -12 | -8 | -5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
16 | Biscay Gulf | TOOT | 340 | 343 | 337 | 127 | 129 | 126 | 291 | 294 | 289 | -1634 | -1618 | -1651 | 0 | 36 | 181 | 380 | 0 | 8 | 42 | 5210 | 5316 | 5104 | 0 | -1639 | -163 | -440 | -129 | -104 | -49 | 1727 | 70 | 16857 | 16857 | 16857 | 92 | 92 | 92
26 | Reschenpass Interconnector Project | TOOT | 19 | 25 | 12 | 15 | 18 | 10 | 3 | 6 | 2 | -193 | -127 | -235 | 0 | 4 | 21 | 10 | 0 | 0 | 1 | 59 | 95 | 28 | 0 | -242 | -13 | -155 | -20 | -15 | -4 | 51 | 2 | 0 | 0 | 0 | 0 | 0 | 0
28 | Italy-Montenegro | PINT | 28 | 29 | 27 | 14 | 16 | 13 | 26 | 29 | 23 | -186 | -172 | -200 | 0 | 4 | 21 | 30 | 0 | 1 | 3 | 431 | 505 | 357 | 0 | -292 | -18 | -223 | -18 | -12 | -6 | 83 | 5 | 0 | 0 | 0 | 0 | 0 | 0
29 | Italy-Tunisia | TOOT | 111 | 118 | 104 | 60 | 60 | 60 | 59 | 64 | 53 | -763 | -763 | -764 | 0 | 17 | 85 | 24 | 0 | 1 | 3 | 955 | 981 | 929 | 0 | -814 | -90 | -97 | -63 | -40 | -27 | -16 | 4 | 4145 | 4145 | 4145 | 25 | 25 | 25
33 | Central Northern Italy | TOOT | 20 | 21 | 18 | 12 | 14 | 10 | 20 | 23 | 17 | -154 | -133 | -176 | 0 | 3 | 17 | 22 | 0 | 0 | 2 | 328 | 352 | 304 | 0 | -161 | -15 | 33 | -17 | -10 | -4 | 56 | 4 | 53 | 53 | 53 | 0 | 0 | 0
35 | CZ Southwest-east corridor | PINT | 31 | 33 | 27 | 9 | 11 | 7 | 10 | 14 | 7 | -120 | -88 | -146 | 0 | 3 | 13 | 72 | 0 | 2 | 8 | 173 | 236 | 120 | 0 | -208 | -14 | -354 | -1 | -14 | -5 | 340 | 13 | 2325 | 2325 | 2325 | 12 | 12 | 12
40 | Belgium-Luxembourg-Germany: long-term perspective | light PINT | 27 | 30 | 22 | 15 | 18 | 9 | 6 | 7 | 5 | -191 | -121 | -231 | 0 | 4 | 21 | N/A | N/A | N/A | N/A | 96 | 110 | 82 | 0 | -276 | -13 | -203 | -23 | -17 | -4 | N/A | N/A | 1547 | 1547 | 1547 | 21 | 21 | 21
47 | Westtirol (AT) - Vöhringen (DE) | PINT | 45 | 51 | 42 | 24 | 31 | 17 | 6 | 10 | 3 | -307 | -217 | -397 | 0 | 7 | 34 | 61 | 0 | 1 | 7 | 96 | 181 | 47 | 0 | -229 | -16 | -98 | -26 | -32 | -4 | 312 | 11 | 2448 | 2448 | 2448 | 14 | 14 | 14
81 | North South Interconnector | TOOT | 67 | 67 | 67 | 30 | 30 | 30 | 31 | 31 | 31 | -379 | -379 | -379 | 0 | 8 | 42 | 19 | 0 | 0 | 2 | 552 | 552 | 552 | 0 | -390 | -47 | 6 | -31 | -20 | -14 | 104 | 3 | 86 | 86 | 86 | 1 | 1 | 1
85 | Integration of RES in Alentejo | TOOT | 14 | 19 | 8 | 1 | 4 | -1 | 23 | 29 | 16 | -15 | 16 | -53 | 0 | 0 | 2 | 20 | 0 | 0 | 2 | 394 | 501 | 288 | 700 | 31 | -6 | 144 | -2 | -1 | -2 | 223 | 4 | 0 | 0 | 0 | 0 | 0 | 0
94 | GerPol Improvements | TOOT | 178 | 181 | 174 | 122 | 128 | 116 | 53 | 59 | 49 | -1559 | -1488 | -1642 | 0 | 34 | 173 | N/A | N/A | N/A | N/A | 895 | 925 | 858 | 0 | -2515 | -14 | -3156 | -193 | -196 | -3 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
103 | Reinforcements Ring NL phase I | TOOT | 28 | 31 | 21 | 13 | 17 | 5 | 9 | 10 | 9 | -163 | -67 | -215 | 0 | 4 | 18 | -12 | 0 | 0 | -1 | 162 | 177 | 135 | 0 | -146 | -19 | 68 | -17 | -12 | -5 | -85 | -2 | 1199 | 1199 | 1199 | 15 | 15 | 15
107 | Celtic Interconnector | TOOT | 189 | 189 | 189 | 65 | 66 | 63 | 105 | 106 | 105 | -828 | -814 | -843 | 0 | 18 | 92 | 174 | 0 | 4 | 19 | 1886 | 1910 | 1862 | 0 | -1375 | -78 | -1319 | -74 | -72 | -25 | 712 | 31 | 5781 | 5781 | 5781 | 59 | 59 | 59
111 | Aurora line (3rd AC Finland-Sweden north) | TOOT | 78 | 82 | 74 | 9 | 12 | 6 | 68 | 75 | 62 | -119 | -75 | -149 | 0 | 3 | 13 | 38 | 0 | 1 | 4 | 1140 | 1288 | 948 | 0 | -387 | -10 | -742 | -16 | -18 | -4 | 146 | 6 | 8436 | 8436 | 8436 | 48 | 48 | 48
120 | Belgian Modular Offshore Grid II (MOG II) | TOOT | 759 | 762 | 756 | 212 | 214 | 208 | 832 | 855 | 809 | -2716 | -2666 | -2745 | 0 | 60 | 301 | 248 | 0 | 5 | 27 | 14687 | 14730 | 14634 | 3500 | -3925 | -303 | -2237 | -261 | -183 | -93 | 826 | 43 | 1603 | 1603 | 1603 | 21 | 21 | 21
121 | Nautilus: multi-purpose interconnector Belgium - UK | PINT | 145 | 145 | 145 | 70 | 70 | 70 | 3 | 3 | 3 | -904 | -904 | -904 | 0 | 20 | 100 | 130 | 0 | 3 | 14 | 51 | 51 | 51 | 0 | -898 | -47 | -1217 | -39 | -101 | -18 | 359 | 23 | 4364 | 4364 | 4364 | 55 | 55 | 55
123 | LitPol Link Stage 2 | TOOT | 191 | 192 | 189 | 164 | 164 | 163 | 44 | 49 | 39 | -2097 | -2091 | -2104 | 0 | 46 | 233 | -22 | N/A | 0 | N/A | 774 | 843 | 705 | 0 | -2636 | -25 | -2653 | -211 | -182 | -5 | -36 | -3 | 4722 | 4722 | 4722 | 42 | 42 | 42
124 | NordBalt phase 2 | PINT | 44 | 47 | 41 | 12 | 12 | 11 | 27 | 29 | 26 | -148 | -143 | -155 | 0 | 3 | 16 | -28 | N/A | -1 | N/A | 453 | 475 | 435 | 0 | -167 | -10 | -176 | -11 | -10 | -3 | -120 | -4 | 1599 | 1599 | 1599 | 15 | 15 | 15
126 | SE North-south short-term reinforcements | TOOT | 132 | 144 | 123 | 29 | 35 | 26 | 52 | 54 | 49 | -372 | -329 | -453 | 0 | 8 | 41 | 32 | 0 | 1 | 4 | 903 | 926 | 879 | 0 | -410 | -34 | -329 | -32 | -31 | -10 | 100 | 7 | 5543 | 5543 | 5543 | 60 | 60 | 60
127 | Central Southern Italy | TOOT | 37 | 45 | 29 | 9 | 11 | 8 | 45 | 50 | 41 | -121 | -98 | -139 | 0 | 3 | 13 | 26 | 0 | 1 | 3 | 752 | 768 | 740 | 0 | -222 | -18 | -115 | -14 | -9 | -6 | 123 | 4 | 1 | 1 | 1 | 0 | 0 | 0
130 | HVDC SuedOstLink Wolmirstedt to area Isar | TOOT | 2008 | 2008 | 2008 | 52 | 52 | 52 | 343 | 343 | 343 | -1858 | -1858 | -1858 | 0 | 41 | 206 | 299 | 0 | -7 | -33 | 3426 | 3426 | 3426 | 0 | -2937 | -2937 | -4085 | -166 | -265 | -25 | 1334 | -49 | 0 | 0 | 0 | 0 | 0 | 0
132 | HVDC Line A-North | TOOT | 5283 | 5283 | 5283 | 129 | 129 | 129 | 896 | 896 | 896 | -4605 | -4605 | -4605 | 0 | 101 | 511 | 718 | 0 | -16 | -80 | 8961 | 8961 | 8961 | 0 | -6860 | -6860 | -7266 | -475 | -496 | -71 | 3004 | -119 | 0 | 0 | 0 | 0 | 0 | 0
138 | Black Sea Corridor | TOOT | 39 | 43 | 33 | 24 | 26 | 22 | 19 | 25 | 15 | -304 | -279 | -334 | 0 | 7 | 34 | N/A | N/A | N/A | N/A | 322 | 380 | 274 | 0 | -282 | -35 | 29 | -24 | -15 | -10 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
142 | CSE4 | TOOT | 11 | 13 | 9 | 5 | 7 | 3 | 10 | 16 | 4 | -68 | -45 | -90 | 0 | 2 | 8 | N/A | N/A | N/A | N/A | 164 | 240 | 81 | 0 | -51 | -3 | -35 | -3 | -2 | -1 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
144 | Mid Continental East corridor | TOOT | 104 | 114 | 89 | 65 | 68 | 61 | 57 | 68 | 48 | -834 | -784 | -867 | 0 | 18 | 93 | -65 | 0 | -1 | -7 | 957 | 1039 | 849 | 0 | -1045 | -73 | -502 | -84 | -55 | -21 | -377 | -10 | 3211 | 3211 | 3211 | 35 | 35 | 35
150 | Italy-Slovenia | light PINT | 41 | 42 | 39 | 33 | 39 | 27 | 10 | 15 | 6 | -429 | -342 | -501 | 0 | 9 | 48 | 66 | 0 | 1 | 7 | 175 | 263 | 86 | 0 | -304 | -42 | 173 | -35 | -18 | -12 | 220 | 11 | 800 | 800 | 800 | 0 | 0 | 0
153 | France-Alderney-Britain | PINT | 272 | 272 | 272 | 123 | 123 | 123 | 30 | 30 | 30 | -1578 | -1578 | -1578 | 0 | 35 | 175 | 226 | 0 | 5 | 25 | 528 | 528 | 528 | 0 | -1909 | -99 | -2216 | -99 | -166 | -34 | 847 | 40 | 6952 | 6952 | 6952 | 78 | 78 | 78
170 | Baltic States Synchronization with Continental Europe | TOOT | 259 | 275 | 240 | 237 | 238 | 235 | 76 | 99 | 58 | -3033 | -3014 | -3052 | 0 | 67 | 337 | -4 | N/A | 0 | N/A | 1274 | 1513 | 1039 | 0 | -3747 | -30 | -4005 | -284 | -252 | -7 | 97 | 0 | 4124 | 4124 | 4124 | 29 | 29 | 29
174 | Greenconnector | PINT | 48 | 52 | 43 | 37 | 40 | 32 | 6 | 7 | 4 | -470 | -409 | -511 | 0 | 10 | 52 | 100 | 0 | 2 | 11 | 99 | 117 | 67 | 0 | -533 | -46 | -169 | -43 | -29 | -14 | 252 | 17 | -1 | -1 | -1 | 0 | 0 | 0
176 | Hansa PowerBridge I | TOOT | 226 | 232 | 219 | 117 | 118 | 115 | 60 | 68 | 52 | -1496 | -1474 | -1518 | 0 | 33 | 166 | N/A | N/A | N/A | N/A | 1047 | 1177 | 916 | 0 | -1881 | -128 | -1056 | -143 | -110 | -38 | N/A | N/A | 3595 | 3595 | 3595 | 44 | 44 | 44
183 | DKW-DE, Westcoast | TOOT | 185 | 192 | 176 | 90 | 95 | 83 | 118 | 126 | 106 | -1158 | -1067 | -1224 | 0 | 25 | 129 | N/A | N/A | N/A | N/A | 2090 | 2294 | 1881 | 0 | -1123 | -105 | -169 | -103 | -74 | -30 | N/A | N/A | 1121 | 1121 | 1121 | 15 | 15 | 15
186 | East of Austria | TOOT | 312 | 320 | 308 | 98 | 100 | 97 | 323 | 324 | 323 | -1254 | -1242 | -1278 | 0 | 28 | 139 | -8 | 0 | 0 | -1 | 5802 | 5849 | 5711 | 2000 | -1576 | -134 | -605 | -120 | -78 | -40 | -44 | -1 | 0 | 0 | 0 | 0 | 0 | 0
187 | St. Peter (AT) - Pleinting (DE) | PINT | 105 | 109 | 98 | 58 | 61 | 58 | 11 | 14 | 8 | -749 | -737 | -783 | 0 | 16 | 83 | 158 | 0 | 3 | 18 | 194 | 223 | 131 | 0 | -1087 | -38 | -1190 | -75 | -94 | -12 | 754 | 28 | 0 | 0 | 0 | 0 | 0 | 0
190 | NorthConnect | TOOT | 532 | 532 | 532 | 248 | 248 | 248 | 43 | 43 | 43 | -3179 | -3179 | -3179 | 0 | 70 | 353 | 27 | 0 | 1 | 3 | 775 | 775 | 775 | 0 | -2994 | -256 | -1808 | -203 | -257 | -81 | 61 | 1 | 26619 | 26619 | 26619 | 118 | 118 | 118
200 | CZ Northwest-South corridor | TOOT | 36 | 38 | 33 | 13 | 14 | 11 | 9 | 13 | 7 | -164 | -136 | -178 | 0 | 4 | 18 | 55 | 0 | 1 | 6 | 150 | 194 | 126 | 0 | -262 | -12 | -262 | -19 | -26 | -4 | 278 | 10 | 2407 | 2407 | 2407 | 12 | 12 | 12
210 | Würmlach (AT) - Somplago (IT) interconnection | TOOT | 10 | 14 | 4 | 9 | 11 | 6 | 3 | 7 | 0 | -114 | -81 | -146 | 0 | 3 | 13 | 3 | 0 | 0 | 0 | 52 | 132 | 6 | 0 | -178 | -11 | -127 | -12 | -9 | -3 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0
219 | EuroAsia Interconnector | TOOT | 414 | 420 | 408 | 167 | 171 | 163 | 334 | 357 | 312 | -2141 | -2090 | -2193 | 0 | 47 | 238 | 262 | 0 | 6 | 29 | 5472 | 5512 | 5432 | 0 | -2185 | -261 | 18 | -181 | -117 | -78 | 860 | 43 | 800 | 800 | 800 | 8 | 8 | 8
225 | 2nd interconnector Belgium - Germany | light PINT | 52 | 54 | 51 | 26 | 32 | 20 | 13 | 14 | 10 | -335 | -257 | -412 | 0 | 7 | 37 | N/A | N/A | N/A | N/A | 214 | 253 | 172 | 0 | -431 | -27 | -207 | -40 | -32 | -7 |  | N/A | 0 | 0 | 0 | 0 | 0 | 0
227 | Transbalkan Corridor | TOOT | 21 | 24 | 15 | 11 | 16 | 5 | 14 | 16 | 13 | -147 | -60 | -206 | 0 | 3 | 16 | 29 | 0 | 1 | 3 | 300 | 464 | 224 | 0 | -190 | -20 | -25 | -15 | -9 | -6 | 38 | 5 | 0 | 0 | 0 | 0 | 0 | 0
228 | Muhlbach - Eichstetten | TOOT | 43 | 45 | 40 | 22 | 24 | 20 | 6 | 8 | 4 | -282 | -256 | -312 | 0 | 6 | 31 | 37 | 0 | 1 | 4 | 103 | 121 | 79 | 0 | -485 | -16 | -496 | -33 | -28 | -5 | 192 | 7 | 2044 | 2044 | 2044 | 20 | 20 | 20
230 | GerPol Power Bridge I | TOOT | 348 | 351 | 345 | 331 | 334 | 329 | 22 | 26 | 17 | -4248 | -4216 | -4280 | 0 | 93 | 472 | N/A | N/A | N/A | N/A | 382 | 454 | 309 | 0 | -6725 | 61 | -10137 | -463 | -531 | 18 | N/A | N/A | 6993 | 6993 | 6993 | 75 | 75 | 75
231 | Beznau - Tiengen | PINT | 29 | 32 | 27 | 15 | 20 | 11 | 7 | 9 | 5 | -195 | -138 | -251 | 0 | 4 | 22 | N/A | N/A | N/A | N/A | 125 | 139 | 94 | 0 | -276 | -20 | -138 | -22 | -17 | -6 | N/A | N/A | 653 | 653 | 653 | 2 | 2 | 2
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Bergrheinfeld West | TOOT | 9782 | 9782 | 9782 | 238 | 238 | 238 | 1689 | 1689 | 1689 | -8496 | -8496 | -8496 | 0 | 187 | 943 | 1065 | 0 | -23 | -118 | 16890 | 16890 | 16890 | 0 | -12217 | -12217 | -12224 | -855 | -867 | -143 | 4053 | -176 | 0 | 0 | 0 | 0 | 0 | 0
239 | Fenno-Skan 1 renewal | light PINT | 32 | 36 | 28 | 4 | 9 | 2 | 35 | 40 | 28 | -58 | -22 | -114 | 0 | 1 | 6 | N/A | N/A | N/A | N/A | 585 | 651 | 489 | 0 | -76 | -6 | -98 | -6 | -6 | -2 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
243 | New 400 kV interconnection line between Serbia and Croatia | light PINT | 8 | 10 | 6 | 5 | 6 | 4 | 4 | 9 | 1 | -68 | -45 | -79 | 0 | 1 | 8 | N/A | N/A | N/A | N/A | 68 | 154 | 24 | 0 | -10 | -8 | 81 | -3 | -2 | -2 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
244 | Vigy - Uchtelfangen area | PINT | 206 | 212 | 201 | 103 | 109 | 96 | 26 | 29 | 23 | -1324 | -1228 | -1403 | 0 | 29 | 147 | 238 | 0 | 5 | 26 | 450 | 513 | 354 | 0 | -2356 | -87 | -2299 | -163 | -140 | -27 | 1132 | 45 | 8130 | 8130 | 8130 | 97 | 97 | 97
247 | AQUIND Interconnector | PINT | 389 | 389 | 389 | 175 | 175 | 175 | 32 | 32 | 32 | -2249 | -2249 | -2249 | 0 | 49 | 250 | 218 | 0 | 5 | 24 | 568 | 568 | 568 | 0 | -2775 | -142 | -3196 | -145 | -240 | -49 | 810 | 38 | 9095 | 9095 | 9095 | 103 | 103 | 103
250 | Merchant line Castasegna (CH) - Mese (IT) | PINT | 13 | 15 | 11 | 8 | 9 | 6 | 3 | 6 | 0 | -99 | -74 | -120 | 0 | 2 | 11 | -2 | 0 | 0 | 0 | 44 | 113 | 6 | 0 | -96 | -9 | -15 | -9 | -6 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252 | Internal Belgian Backbone Center-East: HTLS upgrade Massenhoven-VanEyck-Gramme-Courcelles-Bruegel-Mercator | PINT | [15 empty] | -12 | 0 | 0 | -1 | [10 empty] | -35 | -2 | 0 | 0 | 0 | 0 | 0 | 0
253 | Upstream reinforcement in France to increase FR-CH capacity | PINT | 35 | 38 | 33 | 14 | 15 | 11 | 4 | 7 | 2 | -177 | -146 | -195 | 0 | 4 | 20 | 159 | 0 | 3 | 18 | 66 | 125 | 30 | 0 | -193 | -17 | -135 | -12 | -17 | -5 | 792 | 30 | 4695 | 4695 | 4695 | 38 | 38 | 38
254 | HVDC Ultranet Osterath to Philippsburg | TOOT | 447 | 447 | 447 | 12 | 12 | 12 | 47 | 47 | 47 | -411 | -411 | -411 | 0 | 14 | 50 | 193 | 0 | -4 | -21 | 465 | 465 | 465 | 0 | -626 | -626 | -1053 | -36 | -57 | 1 | 546 | -33 | 0 | 0 | 0 | 0 | 0 | 0
259 | HU-RO | PINT | 46 | 50 | 42 | 24 | 25 | 22 | 25 | 29 | 22 | -302 | -287 | -322 | 0 | 7 | 33 | 90 | 0 | 2 | 10 | 426 | 476 | 375 | 0 | -259 | -33 | -7 | -20 | -14 | -10 | 462 | 16 | 1232 | 1232 | 1232 | 14 | 14 | 14
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | PINT | 215 | 254 | 163 | 52 | 61 | 47 | 24 | 29 | 20 | -673 | -604 | -787 | 0 | 15 | 75 | 284 | 0 | 6 | 31 | 406 | 526 | 309 | 2000 | -549 | -50 | -524 | -27 | -71 | -17 | 776 | 48 | 4785 | 4785 | 4785 | 55 | 55 | 55
263 | Lake Constance East | light PINT | 110 | 111 | 110 | 68 | 72 | 65 | 13 | 15 | 10 | -873 | -833 | -925 | 0 | 19 | 97 | N/A | N/A | N/A | N/A | 223 | 271 | 181 | 0 | -1459 | -26 | -1710 | -107 | -114 | -8 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
267 | Hansa PowerBridge II | light PINT | 197 | 198 | 195 | 108 | 109 | 106 | 55 | 61 | 48 | -1379 | -1362 | -1396 | 0 | 30 | 153 | N/A | N/A | N/A | N/A | 952 | 1053 | 851 | 0 | -1775 | -123 | -906 | -135 | -102 | -37 | N/A | N/A | 2733 | 2733 | 2733 | 16 | 16 | 16
270 | FR-ES project -Aragón-Atlantic Pyrenees | PINT | 184 | 186 | 181 | 64 | 71 | 60 | 170 | 175 | 165 | -822 | -767 | -912 | 0 | 18 | 91 | 376 | 0 | 8 | 42 | 3047 | 3171 | 2976 | 0 | -924 | -91 | -276 | -72 | -61 | -28 | 1524 | 69 | 8017 | 8017 | 8017 | 63 | 63 | 63
276 | FR-ES project -Navarra-Landes | PINT | 184 | 186 | 181 | 64 | 71 | 60 | 170 | 175 | 165 | -822 | -767 | -912 | 0 | 18 | 91 | 373 | 0 | 8 | 41 | 3047 | 3171 | 2976 | 0 | -924 | -91 | -276 | -72 | -61 | -28 | 1523 | 68 | 8017 | 8017 | 8017 | 63 | 63 | 63
280 | FR-BE: study Lonny-Achene-Gramme | PINT | 100 | 102 | 98 | 49 | 54 | 47 | 3 | 7 | 1 | -632 | -602 | -692 | 0 | 14 | 70 | 102 | 0 | 2 | 11 | 61 | 120 | 14 | 0 | -1221 | -45 | -1319 | -73 | -69 | -15 | 465 | 19 | 3464 | 3464 | 3464 | 41 | 41 | 41
283 | TuNur Italy | PINT | 660 | 788 | 572 | 198 | 206 | 190 | 657 | 700 | 614 | -2536 | -2437 | -2636 | 0 | 56 | 282 | 122 | 0 | 3 | 14 | 11752 | 12649 | 10855 | 4900 | -2194 | -312 | 751 | -201 | -128 | -93 | 742 | 21 | 0 | 0 | 0 | 0 | 0 | 0
285 | GridLink | PINT | 272 | 272 | 272 | 123 | 123 | 123 | 30 | 30 | 30 | -1578 | -1578 | -1578 | 0 | 35 | 175 | 238 | 0 | 5 | 26 | 528 | 528 | 528 | 0 | -1978 | -98 | -2337 | -101 | -167 | -34 | 898 | 42 | 6952 | 6952 | 6952 | 78 | 78 | 78
286 | Greenlink | PINT | 107 | 107 | 107 | 39 | 39 | 39 | 74 | 74 | 74 | -499 | -499 | -499 | 0 | 11 | 55 | 33 | 0 | 1 | 4 | 1306 | 1306 | 1306 | 0 | 593 | 27 | 736 | 30 | 52 | 9 | 118 | 6 | 3578 | 3578 | 3578 | 39 | 39 | 39
293 | Southern Aegean Interconnector | PINT | 63 | 66 | 61 | 23 | 25 | 21 | 65 | 68 | 63 | -289 | -272 | -316 | 0 | 6 | 32 | 76 | 0 | 2 | 8 | 1093 | 1136 | 1032 | 582 | -422 | -27 | -230 | -35 | -23 | -8 | 193 | 14 | 0 | 0 | 0 | 0 | 0 | 0
297 | BRABO II + III | TOOT | 33 | 38 | 30 | 18 | 21 | 14 | 22 | 29 | 19 | -229 | -181 | -266 | 0 | 5 | 25 | 109 | 0 | 2 | 12 | 376 | 445 | 330 | 0 | -186 | -13 | -34 | -21 | -17 | -3 | 390 | 19 | 2236 | 2236 | 2236 | 31 | 31 | 31
299 | SACOI3 | TOOT | 79 | 89 | 69 | 31 | 36 | 25 | 57 | 66 | 49 | -400 | -316 | -464 | 0 | 9 | 44 | 27 | 0 | 1 | 3 | 969 | 1023 | 884 | 0 | -426 | -54 | 49 | -36 | -23 | -16 | 116 | 5 | 10418 | 10418 | 10418 | 4 | 4 | 4
309 | NeuConnect | TOOT | 252 | 252 | 252 | 120 | 120 | 120 | 18 | 18 | 18 | -1535 | -1535 | -1535 | 0 | 34 | 170 | 252 | 0 | 6 | 28 | 324 | 324 | 324 | 0 | -1585 | -91 | -1790 | -82 | -150 | -31 | 719 | 41 | 11457 | 11457 | 11457 | 92 | 92 | 92
312 | St. Peter (AT) - Tauern (AT) | TOOT | 176 | 177 | 174 | 90 | 96 | 87 | 28 | 32 | 25 | -1159 | -1116 | -1225 | 0 | 26 | 129 | 181 | 0 | 4 | 20 | 482 | 500 | 461 | 0 | -1874 | -37 | -2335 | -130 | -159 | -12 | 958 | 32 | 12950 | 12950 | 12950 | 47 | 47 | 47
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | TOOT | 182 | 193 | 174 | 95 | 109 | 87 | 25 | 32 | 19 | -1220 | -1116 | -1402 | 0 | 27 | 135 | 207 | 0 | 5 | 23 | 424 | 500 | 324 | 0 | -1874 | -37 | -2335 | -130 | -159 | -12 | 1037 | 37 | 12950 | 12950 | 12950 | 47 | 47 | 47
323 | Dekani (SI) - Zaule (IT) interconnection | TOOT | 2 | 4 | 1 | 2 | 5 | -2 | -2 | 2 | 0 | -23 | 32 | -69 | 0 | 1 | 3 | -3 | 0 | 0 | 0 | -34 | 24 | -149 | 0 | -43 | -3 | -15 | -4 | -2 | -1 | -8 | -1 | 0 | 0 | 0 | 0 | 0 | 0
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | TOOT | 3 | 4 | 0 | 0 | 2 | -4 | 2 | 2 | 1 | 6 | 58 | -19 | 0 | 0 | 0 | -4 | 0 | 0 | 0 | 36 | 44 | 23 | 0 | 23 | -2 | 70 | -1 | 0 | 0 | -15 | -1 | 13 | 13 | 13 | 0 | 0 | 0
325 | Obersielach (AT) - Podlog (SI) | PINT | 19 | 23 | 15 | 14 | 17 | 10 | 4 | 6 | 4 | -180 | -126 | -214 | 0 | 4 | 20 | 49 | 0 | 1 | 5 | 73 | 110 | 56 | 0 | -157 | -20 | 67 | -15 | -4 | -6 | 156 | 8 | 0 | 0 | 0 | 0 | 0 | 0
328 | Interconnector DE-LUX | TOOT | 5 | 8 | 3 | 1 | 2 | -2 | 2 | 3 | 1 | -11 | 21 | -24 | 0 | 0 | 1 | N/A | N/A | N/A | N/A | 27 | 43 | 11 | 0 | -3 | -2 | 0 | 1 | 1 | -1 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [6 empty] | 38 | 2 | 0 | 0 | 0 | 0 | 0 | 0
330 | 4th 400kV CZ-SK interconnector | light PINT | 10 | 13 | 8 | 10 | 13 | 6 | 2 | 5 | 0 | -128 | -72 | -169 | 0 | 3 | 14 | N/A | N/A | N/A | N/A | 31 | 95 | 6 | 0 | -297 | -4 | -306 | -24 | -17 | -1 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
333 | PST Foretaille | PINT | 100 | 104 | 97 | 52 | 55 | 49 | 8 | 12 | 4 | -664 | -624 | -710 | 0 | 15 | 74 | 132 | 0 | 3 | 15 | 135 | 222 | 59 | 0 | -791 | -75 | -200 | -63 | -42 | -22 | 665 | 25 | 584 | 584 | 584 | 4 | 4 | 4
335 | North Sea Wind Power Hub | light PINT | 1005 | 1016 | 990 | 885 | 896 | 875 | 3141 | 3251 | 3013 | -11349 | -11223 | -11491 | 0 | 250 | 1260 | N/A | N/A | N/A | N/A | 55393 | 55884 | 54453 | 12000 | -15708 | -1098 | -9487 | -1104 | -780 | -334 |  | N/A | 0 | 0 | 0 | 0 | 0 | 0
338 | Adriatic HVDC link | PINT | 58 | 76 | 39 | 31 | 37 | 24 | 40 | 54 | 26 | -394 | -310 | -477 | 0 | 9 | 44 | -25 | 0 | -1 | -3 | 644 | 820 | 469 | 0 | -357 | -35 | -96 | -27 | -17 | -11 | -41 | -4 | 0 | 0 | 0 | 0 | 0 | 0
339 | Tyrrhenian link | PINT | 64 | 68 | 61 | 18 | 25 | 12 | 70 | 73 | 67 | -235 | -152 | -317 | 0 | 5 | 26 | 111 | 0 | 2 | 12 | 1148 | 1185 | 1111 | 0 | -343 | -38 | -43 | -26 | -17 | -11 | -214 | 17 | 0 | 0 | 0 | 0 | 0 | 0
340 | Avelgem-Courcelles (Boucle du Hainaut): new corridor | TOOT | [15 empty] | -100 | 0 | -2 | -11 | [10 empty] | -375 | -18 | 0 | 0 | 0 | 0 | 0 | 0
341 | North CSE Corridor | PINT | 37 | 43 | 32 | 21 | 25 | 18 | 19 | 20 | 18 | -267 | -232 | -318 | 0 | 6 | 30 | N/A | N/A | N/A | N/A | 326 | 353 | 303 | 0 | -342 | -23 | -184 | -27 | -18 | -7 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
342 | Central Balkan Corridor | PINT | 22 | 26 | 17 | 14 | 16 | 11 | 9 | 10 | 7 | -181 | -144 | -202 | 0 | 4 | 20 | N/A | N/A | N/A | N/A | 147 | 159 | 125 | 0 | -185 | -11 | -109 | -15 | -10 | -3 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
343 | CSE1 New | PINT | 7 | 11 | 4 | 4 | 5 | 2 | 4 | 6 | 1 | -47 | -30 | -63 | 0 | 1 | 5 | N/A | N/A | N/A | N/A | 69 | 106 | 21 | 0 | -30 | -4 | 8 | -3 | -2 | -1 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
346 | ZuidWest380 NL Oost | PINT | 20 | 21 | 20 | 8 | 11 | 6 | 16 | 21 | 13 | -108 | -77 | -146 | 0 | 2 | 12 | -239 | 0 | -5 | -27 | 271 | 315 | 226 | 0 | -183 | -7 | -174 | -13 | -11 | -2 | -1723 | -49 | 1226 | 1226 | 1226 | 17 | 17 | 17
349 | MaresConnect | PINT | 152 | 152 | 152 | 55 | 55 | 55 | 103 | 103 | 103 | -705 | -705 | -705 | 0 | 16 | 78 | 76 | 0 | 2 | 8 | 1828 | 1828 | 1828 | 0 | 593 | 27 | 736 | 30 | 52 | 9 | 254 | 13 | 4938 | 4938 | 4938 | 55 | 55 | 55
350 | South Balkan Corridor | TOOT | 17 | 27 | 12 | 9 | 14 | 6 | 7 | 9 | 5 | -112 | -83 | -178 | 0 | 2 | 12 | N/A | N/A | N/A | N/A | 189 | 389 | 90 | 0 | -20 | -9 | 120 | -7 | -4 | -2 |  | N/A | 0 | 0 | 0 | 0 | 0 | 0
375 | Lienz (AT) - Veneto region (IT) 220 kV | PINT | 37 | 42 | 33 | 27 | 33 | 20 | 8 | 15 | 3 | -348 | -255 | -418 | 0 | 8 | 39 | 38 | 0 | 1 | 4 | 133 | 267 | 56 | 0 | -601 | -36 | -344 | -47 | -27 | -11 | 144 | 6 | 874 | 874 | 874 | 10 | 10 | 10
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | light PINT | 3 | 4 | 0 | 2 | 4 | 0 | 1 | 1 | 0 | -22 | 6 | -56 | 0 | 0 | 2 | N/A | N/A | N/A | N/A | 10 | 17 | 5 | 0 | -73 | 2 | -158 | -1 | -1 | 0 |  | N/A | 0 | 0 | 0 | 0 | 0 | 0
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | PINT | 19 | 21 | 17 | 8 | 11 | 6 | 19 | 21 | 15 | -106 | -77 | -141 | 0 | 2 | 12 | 26 | 0 | 1 | 3 | 315 | 355 | 273 | 0 | -101 | -5 | -51 | -11 | -10 | -1 | 108 | 5 | 1226 | 1226 | 1226 | 17 | 17 | 17
378 | Transformer Gatica | TOOT | [15 empty] | N/A | N/A | N/A | N/A | [10 empty] | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
379 | Uprate Gatica lines | TOOT | [15 empty] | N/A | N/A | N/A | N/A | [10 empty] | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
1034 | HVDC corridor from Northern Germany to Western Germany | PINT | 7182 | 7182 | 7182 | 163 | 163 | 163 | 1202 | 1202 | 1202 | -5819 | -5819 | -5819 | 0 | 128 | 646 | 1115 | 0 | -25 | -124 | 12027 | 12027 | 12027 | 0 | -8131 | -8131 | -6974 | -610 | -517 | -103 | 5510 | -191 | 0 | 0 | 0 | 0 | 0 | 0
1039 | SE North-south long-term reinforcements | light PINT | 19 | 21 | 18 | 11 | 17 | 4 | -1 | 1 | 0 | -138 | -49 | -214 | 0 | 3 | 15 | N/A | N/A | N/A | N/A | -19 | 11 | -48 | 0 | -253 | -9 | -288 | -17 | -14 | -3 |  | N/A | 0 | 0 | 0 | 0 | 0 | 0
1040 | LirIC | PINT | 112 | 112 | 112 | 43 | 43 | 43 | 81 | 81 | 81 | -546 | -546 | -546 | 0 | 12 | 61 | 20 | 0 | 0 | 2 | 1438 | 1438 | 1438 | 0 | -622 | -24 | -823 | -30 | -55 | -9 | 153 | 3 | 0 | 0 | 0 | 0 | 0 | 0
1041 | GREGY Green Energy Interconnector | PINT | 253 | 254 | 251 | 147 | 153 | 142 | 78 | 102 | 60 | -1889 | -1818 | -1960 | 0 | 42 | 210 | 403 | 0 | 9 | 45 | 1306 | 1553 | 1061 | 0 | -1962 | -230 | -161 | -146 | -92 | -70 | 1331 | 75 | 0 | 0 | 0 | 0 | 0 | 0
1042 | Offshore Wind LT 1 | PINT | 57 | 62 | 52 | 7 | 11 | 4 | 99 | 104 | 95 | -84 | -45 | -145 | 0 | 2 | 9 | -6 | N/A | 0 | N/A | 1649 | 1864 | 1474 | 700 | -74 | -7 | -44 | -5 | -4 | -2 | -153 | -1 | 427 | 427 | 427 | 4 | 4 | 4
1046 | Finnish North-South reinforcement | PINT | 113 | 113 | 113 | 22 | 22 | 22 | 235 | 235 | 235 | -278 | -278 | -278 | 0 | 6 | 31 | -62 | 0 | -1 | -7 | 4178 | 4178 | 4178 | 0 | [6 empty] | -624 | -11 | 0 | 0 | 0 | 0 | 0 | 0
1047 | Emden-Eemshaven | light PINT | 40 | 42 | 38 | 18 | 23 | 12 | 15 | 18 | 13 | -237 | -152 | -301 | 0 | 5 | 26 | N/A | N/A | N/A | N/A | 260 | 313 | 202 | 0 | -197 | -22 | 50 | -23 | -19 | -6 |  | N/A | 1458 | 1458 | 1458 | 19 | 19 | 19
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | PINT | 611 | 623 | 599 | 247 | 248 | 245 | 509 | 517 | 502 | -3162 | -3147 | -3177 | 0 | 70 | 351 | 776 | 0 | 17 | 86 | 9149 | 9210 | 9060 | 0 | -3256 | -374 | -186 | -258 | -163 | -112 | 2401 | 142 | N/A | N/A | N/A | N/A | N/A | N/A
1049 | Cronos Energy Ltd | PINT | 166 | 166 | 166 | 78 | 78 | 78 | 22 | 22 | 22 | -999 | -999 | -999 | 0 | 22 | 111 | 104 | 0 | 2 | 12 | 385 | 385 | 385 | 0 | -755 | -60 | -782 | -41 | -103 | -21 | 274 | 18 | 4364 | 4364 | 4364 | 55 | 55 | 55
1050 | Tarchon Energy Ltd | PINT | 207 | 207 | 207 | 103 | 103 | 103 | 22 | 22 | 22 | -1318 | -1318 | -1318 | 0 | 29 | 146 | 142 | 0 | 3 | 16 | 395 | 395 | 395 | 0 | -1070 | -82 | -931 | -69 | -127 | -27 | 431 | 23 | 5792 | 5792 | 5792 | 67 | 67 | 67
1051 | Aminth Energy Ltd | PINT | 305 | 305 | 305 | 136 | 136 | 136 | 120 | 120 | 120 | -1743 | -1743 | -1743 | 0 | 38 | 194 | 38 | 0 | 1 | 4 | 2117 | 2117 | 2117 | 0 | -1318 | -102 | -1115 | -78 | -121 | -34 | 113 | 6 | 5364 | 5364 | 5364 | 60 | 60 | 60
1052 | Lienz (AT) - Obersielach (AT) | PINT | 17 | 20 | 16 | 14 | 17 | 10 | 4 | 6 | 3 | -175 | -126 | -214 | 0 | 4 | 19 | 41 | 0 | 1 | 5 | 75 | 110 | 56 | 0 | -157 | -20 | 67 | -15 | -4 | -6 | 137 | 7 | 0 | 0 | 0 | 0 | 0 | 0
1054 | Westtirol (AT) - Zell/Ziller (AT) | PINT | 45 | 51 | 42 | 24 | 29 | 17 | 6 | 10 | 3 | -302 | -217 | -376 | 0 | 7 | 34 | 78 | 0 | 2 | 9 | 103 | 181 | 59 | 0 | -229 | -16 | -98 | -26 | -32 | -4 | 362 | 14 | 2448 | 2448 | 2448 | 14 | 14 | 14
1055 | Interconnection of Crete to the Mainland System of Greece | TOOT | 274 | 274 | 274 | 90 | 97 | 79 | 265 | 288 | 249 | -1151 | -1014 | -1245 | 0 | 25 | 128 | 102 | 0 | 2 | 11 | 4474 | 4541 | 4385 | 0 | -1691 | -145 | -801 | -111 | -70 | -45 | 381 | 18 | 0 | 0 | 0 | 0 | 0 | 0
1058 | HVDC Interconnector DE-CH | light PINT | 86 | 87 | 84 | 57 | 65 | 48 | 16 | 23 | 9 | -733 | -612 | -827 | 0 | 16 | 81 | N/A | N/A | N/A | N/A | 268 | 421 | 163 | 0 | -749 | -34 | -471 | -78 | -78 | -9 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
1059 | Southern Italy | PINT | 8 | 10 | 3 | 2 | 3 | 1 | 8 | 11 | 5 | -28 | -7 | -41 | 0 | 1 | 3 | -10 | 0 | 0 | -1 | 143 | 204 | 82 | 0 | 373 | -2 | 666 | 9 | 5 | 0 | -36 | -2 | 0 | 0 | 0 | 0 | 0 | 0
1066 | Bulgaria - Turkey | light PINT | 177 | 180 | 174 | 155 | 182 | 131 | 19 | 30 | 12 | -1992 | -1681 | -2340 | 0 | 44 | 221 | -52 | 0 | -1 | -6 | 321 | 451 | 210 | 0 | -3226 | -57 | -4731 | -111 | -73 | -24 | -221 | -9 | 0 | 0 | 0 | 0 | 0 | 0
1067 | New AC 400 kV interconnection line Greece - Turkey | light PINT | 111 | 112 | 110 | 89 | 92 | 85 | 22 | 29 | 16 | -1141 | -1090 | -1179 | 0 | 25 | 127 | N/A | N/A | N/A | N/A | 360 | 447 | 279 | 0 | -1770 | -33 | -2568 | -62 | -41 | -14 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0
1068 | LaSGo Link | light PINT | 47 | 52 | 43 | 12 | 15 | 9 | 21 | 25 | 17 | -156 | -118 | -187 | 0 | 3 | 17 | -3 | 0 | 0 | 4 | 348 | 388 | 304 | 0 | 245 | -14 | 605 | -3 | -5 | -3 | 34 | 0 | 1220 | 1220 | 1220 | 11 | 11 | 11
1074 | Pannonian Corridor | PINT | 10 | 13 | 7 | 7 | 9 | 5 | 2 | 3 | 0 | -92 | -67 | -120 | 0 | 2 | 10 | -52 | 0 | -1 | -6 | 24 | 50 | 8 | 0 | 369 | -9 | 757 | 6 | 3 | -2 | -221 | -9 | 681 | 681 | 681 | 8 | 8 | 8
1082 | Sea-Socket | light PINT | 107 | 109 | 104 | 32 | 34 | 29 | 108 | 110 | 106 | -404 | -371 | -441 | 0 | 9 | 45 | N/A | N/A | N/A | N/A | 1913 | 1934 | 1887 | 700 | -482 | -46 | -161 | -35 | -26 | -14 | N/A | N/A | 353 | 353 | 353 | 4 | 4 | 4
1085 | Malta-Italy Cable Link No.2 | PINT | 7 | 10 | 4 | 2 | 3 | 1 | 2 | 3 | 1 | -22 | -14 | -38 | 0 | 0 | 2 | 33 | 0 | 1 | 4 | 33 | 51 | 12 | 0 | 387 | -5 | 735 | 8 | 4 | 0 | 94 | 6 | 99 | 99 | 99 | 1 | 1 | 1
1086 | Estonia internal grid reinforcement to increase RES connection capability (RRF project) | PINT | 54 | 61 | 51 | 6 | 10 | 4 | 85 | 86 | 84 | -80 | -52 | -131 | 0 | 2 | 9 | -3 | 0 | 0 | 28 | 1425 | 1492 | 1309 | 700 | 305 | -7 | 563 | 5 | 1 | -1 | -11 | 0 | 644 | 644 | 644 | 6 | 6 | 6
1088 | Latvia and Estonia Hybrid Off-Shore interconnector | PINT | 2 | 3 | 1 | 7 | 8 | 6 | 149 | 152 | 146 | -85 | -78 | -97 | 0 | 2 | 9 | -1 | 0 | 0 | 28 | 2514 | 2688 | 2344 | 1000 | 274 | -9 | 463 | 2 | -4 | -2 | -77 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1092 | Triton Link: offshore hybrid HVDC interconnector Belgium – Denmark | PINT | 267 | 270 | 264 | 201 | 204 | 198 | 693 | 715 | 667 | -2580 | -2539 | -2616 | 0 | 57 | 286 | 256 | 0 | 6 | 28 | 12218 | 12307 | 12066 | 3000 | -3622 | -264 | -2157 | -250 | -187 | -81 | 898 | 43 | 0 | 0 | 0 | 0 | 0 | 0
1094 | Estlink 3 | light PINT | 54 | 57 | 50 | 13 | 15 | 11 | 34 | 42 | 29 | -172 | -145 | -192 | 0 | 4 | 19 | -11 | 0 | 0 | 13 | 557 | 646 | 510 | 0 | 272 | -17 | 541 | -3 | -9 | -4 | -28 | -1 | 1200 | 1200 | 1200 | 12 | 12 | 12
1095 | Aurora line 2 (4th AC Finland-Sweden north) | light PINT | 50 | 56 | 46 | 8 | 11 | 5 | 48 | 49 | 46 | -103 | -58 | -143 | 0 | 2 | 11 | N/A | N/A | N/A | N/A | 795 | 824 | 753 | 0 | -299 | -7 | -507 | -14 | -13 | -2 |  | N/A | 2385 | 2385 | 2385 | 21 | 21 | 21
1096 | Beznau - Mettlen | PINT | 31 | 36 | 28 | 16 | 20 | 7 | 10 | 12 | 6 | -206 | -85 | -257 | 0 | 5 | 23 | 94 | 0 | 2 | 10 | 170 | 216 | 108 | 0 | -138 | -24 | 110 | -15 | -10 | -7 | 404 | 16 | 5 | 5 | 5 | 0 | 0 | 0
1097 | Upgrade to Konti-Skan | PINT | 99 | 110 | 86 | 52 | 58 | 45 | 38 | 41 | 35 | -661 | -573 | -741 | 0 | 15 | 73 | 117 | 0 | 3 | 13 | 638 | 646 | 629 | 0 | -1032 | -50 | -865 | -69 | -52 | -15 | 466 | 20 | 2398 | 2398 | 2398 | 28 | 28 | 28
1098 | Offshore Wind LT 2 | PINT | 58 | 62 | 54 | 7 | 11 | 5 | 101 | 103 | 97 | -93 | -60 | -145 | 0 | 2 | 10 | 0 | N/A | 0 | N/A | 1651 | 1854 | 1474 | 700 | -136 | -11 | -108 | -7 | -4 | -4 | -84 | 0 | 427 | 427 | 427 | 4 | 4 | 4
1100 | Reinforcement of the existing CZ-DE interconnector (Hradec - Röhrsdorf) on the CZ side | PINT | 19 | 19 | 19 | 9 | 11 | 8 | 8 | 10 | 6 | -116 | -100 | -139 | 0 | 3 | 13 | 94 | 0 | 2 | 10 | 138 | 154 | 109 | 0 | -90 | -13 | 28 | -8 | -5 | -4 | 404 | 16 | -1 | -1 | -1 | 0 | 0 | 0
1102 | Mettlen - Ulrichen | light PINT | 10 | 14 | 7 | 6 | 8 | 5 | 2 | 2 | 1 | -78 | -68 | -97 | 0 | 2 | 9 | 16 | 0 | 0 | 2 | 28 | 35 | 23 | 0 | -55 | -7 | 3 | -4 | -3 | -2 | 80 | 3 | 5 | 5 | 5 | 0 | 0 | 0
1103 | Bickigen - Chippis | PINT | 21 | 23 | 19 | 13 | 15 | 11 | 6 | 8 | 5 | -171 | -146 | -191 | 0 | 4 | 19 | 147 | 0 | 4 | 17 | 96 | 126 | 80 | 0 | -135 | -18 | 41 | -13 | -8 | -5 | 438 | 24 | 5 | 5 | 5 | 0 | 0 | 0
1104 | Niederstedem - Roost | PINT | 1 | 3 | 0 | 1 | 3 | 0 | 2 | 7 | 0 | -15 | 0 | -39 | 0 | 0 | 2 | 147 | 0 | 4 | 17 | 42 | 124 | 0 | 0 | 19 | -1 | 38 | 1 | 0 | 0 | 438 | 24 | 5 | 5 | 5 | 0 | 0 | 0
1105 | Georgia-Romania Black Sea (submarine) interconnection cable project | PINT | 105 | 110 | 100 | 57 | 65 | 47 | 33 | 40 | 30 | -733 | -601 | -834 | 0 | 16 | 81 | 16 | 0 | 0 | 2 | 563 | 601 | 542 | 0 | -788 | -97 | 50 | -66 | -42 | -29 | 80 | 3 | 0 | 0 | 0 | 0 | 0 | 0
1106 | Bornholm Energy Island (BEI) | TOOT | 182 | 186 | 175 | 167 | 170 | 165 | 454 | 468 | 445 | -2144 | -2110 | -2182 | 0 | 47 | 238 | 147 | 0 | 4 | 17 | 8011 | 8043 | 7960 | 2000 | -1999 | -201 | -156 | -183 | -128 | -59 | 438 | 24 | 0 | 0 | 0 | 0 | 0 | 0
1107 | EuroAfrica Interconnector | PINT | 95 | 112 | 78 | 35 | 43 | 31 | 54 | 61 | 45 | -451 | -395 | -553 | 0 | 10 | 50 | -20 | 0 | 0 | -2 | 901 | 965 | 809 | 0 | -400 | -46 | -37 | -31 | -22 | -14 | -65 | -4 | 0 | 0 | 0 | 0 | 0 | 0
1109 | Basilicata - Campania reinforcements | PINT | 10 | 13 | 8 | 3 | 7 | 0 | 12 | 13 | 12 | -44 | 4 | -91 | 0 | 1 | 5 | -14 | 0 | 0 | -2 | 200 | 203 | 196 | 0 | -86 | -5 | -84 | -4 | -3 | -2 | -46 | -2 | 5 | 5 | 5 | 0 | 0 | 0
1110 | Sicily - Calabria | PINT | 6 | 9 | 3 | 3 | 4 | 2 | 2 | 3 | 2 | -36 | -21 | -51 | 0 | 1 | 4 | 9 | 0 | 0 | 1 | 38 | 48 | 27 | 0 | -14 | -2 | 0 | -1 | -1 | 0 | 32 | 2 | 14 | 14 | 14 | 42 | 42 | 42
1112 | GRITA 2 | PINT | 52 | 55 | 50 | 21 | 23 | 20 | 41 | 45 | 39 | -275 | -257 | -293 | 0 | 6 | 31 | 9 | 0 | 0 | 1 | 701 | 731 | 678 | 0 | -246 | -31 | 21 | -20 | -13 | -9 | 37 | 2 | 0 | 0 | 0 | 0 | 0 | 0
1119 | Bisamberg (AT) - Wien SO (AT) - Parndorf (AT) | PINT | 357 | 357 | 357 | 114 | 114 | 114 | 374 | 374 | 374 | -1459 | -1459 | -1459 | 0 | 32 | 162 | -34 | 0 | -1 | -4 | 6752 | 6752 | 6752 | 3000 | [6 empty] | -131 | -6 | 0 | 0 | 0 | 0 | 0 | 0
1120 | Wien SO (AT) – Ternitz (AT) – Hessenberg (AT) | PINT | 90 | 90 | 90 | 34 | 34 | 34 | 95 | 95 | 95 | -432 | -432 | -432 | 0 | 10 | 48 | -21 | 0 | 0 | -2 | 1720 | 1720 | 1720 | 750 | [6 empty] | -66 | -4 | 0 | 0 | 0 | 0 | 0 | 0
1121 | Hessenberg (AT) - Weißenbach (AT) | PINT | 68 | 68 | 68 | 20 | 20 | 20 | 73 | 73 | 73 | -257 | -257 | -257 | 0 | 6 | 29 | -22 | 0 | 0 | -2 | 1315 | 1315 | 1315 | 600 | [6 empty] | -63 | -4 | 0 | 0 | 0 | 0 | 0 | 0
1122 | Offshore Wind connection Centre Manche 1 | TOOT | 217 | 221 | 209 | 50 | 54 | 46 | 284 | 290 | 279 | -647 | -589 | -686 | 0 | 14 | 72 | 119 | 0 | 3 | 13 | 5133 | 5228 | 5048 | 1250 | -769 | -82 | -121 | -60 | -40 | -25 | 497 | 22 | 1425 | 1425 | 1425 | 19 | 19 | 19
1123 | Offshore Wind Connection Centre Manche 2 | PINT | 217 | 221 | 209 | 50 | 54 | 46 | 284 | 290 | 279 | -647 | -589 | -686 | 0 | 14 | 72 | 132 | 0 | 3 | 15 | 5133 | 5228 | 5048 | 1250 | -769 | -82 | -121 | -60 | -40 | -25 | 523 | 24 | 1425 | 1425 | 1425 | 19 | 19 | 19
1124 | Offshore Wind Connection South Britanny | TOOT | 132 | 133 | 132 | 30 | 32 | 26 | 179 | 195 | 167 | -385 | -329 | -413 | 0 | 8 | 43 | 12 | 0 | 0 | 1 | 3023 | 3069 | 2970 | 750 | -504 | -47 | -171 | -37 | -25 | -14 | 53 | 2 | 843 | 843 | 843 | 11 | 11 | 11
1125 | Offshore Wind Connection Occitanie | TOOT | 132 | 133 | 132 | 30 | 32 | 26 | 179 | 195 | 167 | -385 | -329 | -413 | 0 | 8 | 43 | -4 | 0 | 0 | 0 | 3023 | 3069 | 2970 | 750 | -504 | -47 | -171 | -37 | -25 | -14 | -28 | -1 | 843 | 843 | 843 | 11 | 11 | 11
1126 | Offshore Wind Connection PACA | TOOT | 132 | 133 | 132 | 30 | 32 | 26 | 179 | 195 | 167 | -385 | -329 | -413 | 0 | 8 | 43 | -18 | 0 | 0 | -2 | 3023 | 3069 | 2970 | 750 | -504 | -47 | -171 | -37 | -25 | -14 | -98 | -3 | 843 | 843 | 843 | 11 | 11 | 11
1127 | Offshore Wind Connection South Atlantic | PINT | 216 | 217 | 215 | 53 | 55 | 52 | 295 | 313 | 279 | -685 | -662 | -709 | 0 | 15 | 76 | 89 | 0 | 2 | 10 | 5004 | 5193 | 4767 | 1250 | -796 | -75 | -268 | -58 | -39 | -23 | 391 | 16 | 1351 | 1351 | 1351 | 18 | 18 | 18
1129 | New RES at Minho region | TOOT | 29 | 33 | 24 | 6 | 8 | 4 | 34 | 38 | 30 | -76 | -56 | -97 | 0 | 2 | 8 | 9 | 0 | 0 | 1 | 577 | 633 | 526 | 400 | -85 | -14 | 50 | -8 | -5 | -4 | 55 | 2 | 0 | 0 | 0 | 0 | 0 | 0

## 2040DE
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_market_SEW |  |  | ΔRES |  |  | ΔRES_MW
|  |  | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | low | mid | high | weighted avg | max | min | Explicit
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW
1 | RES in north of Portugal | TOOT | 85 | 89 | 80 | 11 | 16 | 8 | 67 | 77 | 60 | -92 | -61 | -130 | 3 | 13 | 34 | 1443 | 1625 | 1273 | 1154
4 | Interconnection Portugal-Spain | TOOT | 36 | 49 | 25 | 6 | 9 | 3 | 29 | 34 | 23 | -53 | -27 | -70 | 2 | 8 | 20 | 629 | 717 | 508 | 0
16 | Biscay Gulf | TOOT | 331 | 354 | 298 | 72 | 78 | 67 | 207 | 220 | 189 | -589 | -543 | -632 | 19 | 86 | 221 | 4440 | 4677 | 4164 | 0
26 | Reschenpass Interconnector Project | TOOT | 61 | 65 | 54 | 14 | 17 | 10 | 32 | 35 | 28 | -117 | -81 | -138 | 4 | 17 | 44 | 681 | 761 | 587 | 0
28 | Italy-Montenegro | PINT | 65 | 100 | 36 | 14 | 22 | 9 | 28 | 42 | 18 | -137 | -100 | -178 | 4 | 17 | 44 | 541 | 712 | 392 | 0
29 | Italy-Tunisia | TOOT | 254 | 258 | 250 | 107 | 111 | 103 | 86 | 89 | 83 | -870 | -840 | -900 | 29 | 127 | 326 | 1862 | 1958 | 1765 | 0
33 | Central Northern Italy | TOOT | 27 | 39 | 11 | 9 | 13 | 3 | 21 | 22 | 20 | -75 | -42 | -106 | 2 | 10 | 26 | 424 | 474 | 343 | 0
35 | CZ Southwest-east corridor | PINT | 48 | 52 | 46 | 9 | 11 | 7 | 36 | 39 | 31 | -71 | -54 | -93 | 2 | 10 | 27 | 765 | 807 | 684 | 0
40 | Belgium-Luxembourg-Germany: long-term perspective | light PINT | 57 | 60 | 54 | 12 | 13 | 11 | 35 | 39 | 29 | -101 | -93 | -108 | 3 | 15 | 38 | 739 | 796 | 651 | 0
47 | Westtirol (AT) - Vöhringen (DE) | PINT | 70 | 74 | 67 | 18 | 22 | 16 | 35 | 37 | 33 | -167 | -137 | -223 | 5 | 22 | 55 | 701 | 761 | 623 | 0
81 | North South Interconnector | TOOT | 145 | 168 | 115 | 46 | 47 | 46 | 70 | 79 | 64 | -376 | -374 | -379 | 12 | 55 | 141 | 1497 | 1667 | 1357 | 0
85 | Integration of RES in Alentejo | TOOT | 10 | 15 | 6 | 1 | 3 | -1 | 7 | 10 | 4 | -9 | 4 | -28 | 0 | 1 | 3 | 147 | 208 | 75 | 700
94 | GerPol Improvements | TOOT | 225 | 227 | 224 | 86 | 91 | 80 | 103 | 106 | 100 | -697 | -654 | -740 | 23 | 102 | 261 | 2229 | 2249 | 2208 | 0
103 | Reinforcements Ring NL phase I | TOOT | 62 | 67 | 54 | 13 | 16 | 10 | 32 | 34 | 31 | -107 | -82 | -129 | 4 | 16 | 40 | 674 | 701 | 652 | 0
107 | Celtic Interconnector | TOOT | 185 | 192 | 180 | 45 | 45 | 45 | 101 | 108 | 94 | -367 | -363 | -370 | 12 | 54 | 138 | 2161 | 2304 | 2077 | 0
111 | Aurora line (3rd AC Finland-Sweden north) | TOOT | 111 | 114 | 106 | 3 | 5 | 2 | 94 | 108 | 79 | -24 | -14 | -39 | 1 | 4 | 9 | 2002 | 2237 | 1731 | 0
120 | Belgian Modular Offshore Grid II (MOG II) | TOOT | 493 | 648 | 327 | 58 | 77 | 33 | 497 | 568 | 420 | -469 | -272 | -630 | 15 | 69 | 176 | 10588 | 12003 | 8689 | 3500
121 | Nautilus: multi-purpose interconnector Belgium - UK | PINT | 142 | 148 | 137 | 21 | 24 | 17 | 50 | 56 | 42 | -168 | -141 | -198 | 6 | 25 | 63 | 1064 | 1193 | 926 | 0
123 | LitPol Link Stage 2 | TOOT | 167 | 180 | 157 | 84 | 88 | 81 | 50 | 52 | 47 | -682 | -662 | -718 | 23 | 100 | 256 | 1064 | 1119 | 1032 | 0
124 | NordBalt phase 2 | PINT | 53 | 57 | 45 | 3 | 6 | -2 | 43 | 54 | 32 | -25 | 12 | -51 | 1 | 4 | 10 | 919 | 1126 | 700 | 0
126 | SE North-south short-term reinforcements | TOOT | 80 | 83 | 78 | 16 | 18 | 13 | 51 | 63 | 34 | -128 | -106 | -144 | 4 | 19 | 48 | 1087 | 1358 | 749 | 0
127 | Central Southern Italy | TOOT | 45 | 53 | 36 | 4 | 6 | 0 | 41 | 52 | 28 | -35 | -3 | -51 | 1 | 5 | 13 | 730 | 834 | 626 | 0
130 | HVDC SuedOstLink Wolmirstedt to area Isar | TOOT | 2107 | 2107 | 2107 | 27 | 27 | 27 | 403 | 403 | 403 | -982 | -982 | -982 | 103 | 455 | 1168 | 4027 | 4027 | 4027 | 0
132 | HVDC Line A-North | TOOT | 6300 | 6300 | 6300 | 82 | 82 | 82 | 1146 | 1146 | 1146 | -2935 | -2935 | -2935 | 97 | 429 | 1101 | 11460 | 11460 | 11460 | 0
138 | Black Sea Corridor | TOOT | 60 | 61 | 57 | 15 | 18 | 10 | 36 | 41 | 34 | -118 | -83 | -149 | 4 | 17 | 44 | 774 | 849 | 714 | 0
142 | CSE4 | TOOT | 43 | 44 | 43 | 11 | 14 | 8 | 24 | 25 | 22 | -93 | -62 | -113 | 3 | 14 | 35 | 502 | 556 | 459 | 0
144 | Mid Continental East corridor | TOOT | 104 | 111 | 98 | 19 | 24 | 15 | 72 | 74 | 70 | -157 | -122 | -197 | 5 | 23 | 59 | 1533 | 1578 | 1472 | 0
150 | Italy-Slovenia | light PINT | 143 | 148 | 135 | 42 | 47 | 37 | 62 | 65 | 60 | -342 | -305 | -379 | 11 | 50 | 128 | 1339 | 1428 | 1274 | 0
153 | France-Alderney-Britain | PINT | 267 | 280 | 247 | 56 | 58 | 53 | 126 | 130 | 118 | -455 | -432 | -470 | 15 | 66 | 171 | 2710 | 2781 | 2598 | 0
170 | Baltic States Synchronization with Continental Europe | TOOT | 220 | 222 | 219 | 115 | 120 | 111 | 67 | 74 | 59 | -938 | -904 | -976 | 31 | 137 | 352 | 1437 | 1576 | 1230 | 0
174 | Greenconnector | PINT | 124 | 136 | 107 | 37 | 39 | 33 | 47 | 48 | 45 | -300 | -272 | -319 | 10 | 44 | 112 | 1002 | 1050 | 950 | 0
176 | Hansa PowerBridge I | TOOT | 149 | 172 | 118 | 36 | 39 | 33 | 90 | 107 | 67 | -291 | -267 | -314 | 10 | 42 | 109 | 1922 | 2286 | 1472 | 0
183 | DKW-DE, Westcoast | TOOT | 97 | 103 | 91 | 27 | 30 | 25 | 63 | 70 | 58 | -223 | -202 | -247 | 7 | 33 | 84 | 1337 | 1488 | 1225 | 0
186 | East of Austria | TOOT | 134 | 139 | 131 | 15 | 21 | 7 | 134 | 141 | 123 | -124 | -58 | -174 | 4 | 18 | 46 | 2872 | 2986 | 2706 | 2000
187 | St. Peter (AT) - Pleinting (DE) | PINT | 178 | 181 | 175 | 47 | 51 | 39 | 94 | 99 | 89 | -380 | -317 | -416 | 13 | 55 | 142 | 1991 | 2126 | 1871 | 0
190 | NorthConnect | TOOT | 404 | 458 | 328 | 84 | 93 | 78 | 179 | 222 | 145 | -687 | -631 | -758 | 23 | 100 | 258 | 4448 | 6177 | 3199 | 0
200 | CZ Northwest-South corridor | TOOT | 51 | 53 | 46 | 9 | 11 | 8 | 35 | 39 | 31 | -75 | -65 | -93 | 2 | 11 | 28 | 750 | 804 | 684 | 0
210 | Würmlach (AT) - Somplago (IT) interconnection | TOOT | 32 | 40 | 27 | 8 | 14 | 1 | 15 | 18 | 10 | -67 | -19 | -113 | 2 | 10 | 25 | 302 | 393 | 218 | 0
219 | EuroAsia Interconnector | TOOT | 679 | 703 | 655 | 228 | 234 | 221 | 297 | 301 | 293 | -1851 | -1799 | -1902 | 61 | 270 | 694 | 6431 | 6458 | 6403 | 0
225 | 2nd interconnector Belgium - Germany | light PINT | 114 | 117 | 110 | 22 | 26 | 19 | 64 | 71 | 57 | -182 | -152 | -211 | 6 | 27 | 68 | 1352 | 1474 | 1248 | 0
227 | Transbalkan Corridor | TOOT | 26 | 32 | 23 | 3 | 6 | 1 | 21 | 24 | 16 | -23 | -11 | -49 | 1 | 3 | 9 | 446 | 522 | 345 | 0
228 | Muhlbach - Eichstetten | TOOT | 45 | 50 | 39 | 10 | 11 | 9 | 26 | 28 | 25 | -82 | -70 | -89 | 3 | 12 | 31 | 554 | 575 | 539 | 0
230 | GerPol Power Bridge I | TOOT | 445 | 456 | 431 | 226 | 230 | 221 | 111 | 112 | 109 | -1838 | -1800 | -1866 | 61 | 268 | 689 | 2359 | 2388 | 2306 | 0
231 | Beznau - Tiengen | PINT | 57 | 60 | 55 | 10 | 17 | 7 | 48 | 54 | 39 | -79 | -53 | -141 | 3 | 11 | 29 | 1020 | 1117 | 868 | 0
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Bergrheinfeld West | TOOT | 7723 | 7723 | 7723 | 105 | 105 | 105 | 1407 | 1407 | 1407 | -3738 | -3738 | -3738 | 33 | 145 | 371 | 14075 | 14075 | 14075 | 0
239 | Fenno-Skan 1 renewal | light PINT | 51 | 57 | 45 | -1 | 1 | -5 | 41 | 42 | 40 | 11 | 37 | -11 | 0 | 0 | 0 | 890 | 895 | 885 | 0
243 | New 400 kV interconnection line between Serbia and Croatia | light PINT | 10 | 14 | 6 | 1 | 2 | -1 | 6 | 8 | 3 | -12 | 8 | -23 | 0 | 1 | 3 | 122 | 174 | 65 | 0
244 | Vigy - Uchtelfangen area | PINT | 234 | 239 | 229 | 52 | 54 | 49 | 134 | 141 | 127 | -422 | -395 | -442 | 14 | 62 | 158 | 2850 | 2915 | 2799 | 0
247 | AQUIND Interconnector | PINT | 388 | 401 | 362 | 81 | 83 | 78 | 183 | 190 | 170 | -660 | -632 | -676 | 22 | 96 | 247 | 3943 | 4047 | 3761 | 0
250 | Merchant line Castasegna (CH) - Mese (IT) | PINT | 18 | 23 | 10 | 6 | 16 | 1 | 6 | 9 | 0 | -49 | -14 | -128 | 2 | 7 | 18 | 125 | 191 | -19 | 0
252 | Internal Belgian Backbone Center-East: HTLS upgrade Massenhoven-VanEyck-Gramme-Courcelles-Bruegel-Mercator | PINT
253 | Upstream reinforcement in France to increase FR-CH capacity | PINT | 59 | 66 | 51 | 16 | 17 | 14 | 21 | 31 | 15 | -147 | -114 | -197 | 4 | 21 | 47 | 357 | 457 | 254 | 0
254 | HVDC Ultranet Osterath to Philippsburg | TOOT | 783 | 783 | 783 | 6 | 6 | 6 | 221 | 221 | 221 | -200 | -200 | -200 | 97 | 431 | 1107 | 2211 | 2211 | 2211 | 0
259 | HU-RO | PINT | 71 | 78 | 68 | 10 | 12 | 8 | 48 | 51 | 46 | -83 | -66 | -96 | 3 | 12 | 31 | 1028 | 1076 | 983 | 0
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | PINT | 153 | 183 | 129 | 28 | 34 | 22 | 48 | 59 | 38 | -229 | -177 | -280 | 8 | 33 | 86 | 1037 | 1252 | 815 | 2000
263 | Lake Constance East | light PINT | 160 | 169 | 155 | 43 | 48 | 35 | 75 | 77 | 71 | -348 | -286 | -393 | 11 | 51 | 130 | 1602 | 1688 | 1503 | 0
267 | Hansa PowerBridge II | light PINT | 145 | 148 | 143 | 30 | 32 | 28 | 73 | 86 | 58 | -246 | -227 | -257 | 8 | 36 | 92 | 1553 | 1778 | 1279 | 0
270 | FR-ES project -Aragón-Atlantic Pyrenees | PINT | 199 | 201 | 196 | 44 | 47 | 39 | 133 | 145 | 126 | -358 | -318 | -386 | 12 | 52 | 134 | 2841 | 3078 | 2656 | 0
276 | FR-ES project -Navarra-Landes | PINT | 199 | 201 | 196 | 44 | 47 | 39 | 133 | 145 | 126 | -358 | -318 | -386 | 12 | 52 | 134 | 2841 | 3078 | 2656 | 0
280 | FR-BE: study Lonny-Achene-Gramme | PINT | 133 | 140 | 124 | 36 | 38 | 33 | 54 | 58 | 49 | -290 | -268 | -312 | 10 | 42 | 109 | 1164 | 1237 | 1072 | 0
283 | TuNur Italy | PINT | 439 | 444 | 432 | 55 | 88 | 16 | 403 | 496 | 343 | -476 | -223 | -718 | 15 | 65 | 167 | 7918 | 8352 | 7552 | 4900
285 | GridLink | PINT | 267 | 280 | 247 | 56 | 58 | 53 | 126 | 130 | 118 | -455 | -432 | -470 | 15 | 66 | 171 | 2710 | 2781 | 2598 | 0
286 | Greenlink | PINT | 97 | 101 | 88 | 26 | 28 | 23 | 44 | 45 | 42 | -212 | -187 | -226 | 7 | 31 | 80 | 925 | 990 | 892 | 0
293 | Southern Aegean Interconnector | PINT | 28 | 30 | 26 | 4 | 6 | 2 | 27 | 31 | 22 | -31 | -14 | -46 | 1 | 4 | 11 | 563 | 656 | 486 | 582
297 | BRABO II + III | TOOT | 34 | 38 | 32 | 7 | 8 | 4 | 24 | 25 | 23 | -56 | -30 | -69 | 2 | 8 | 21 | 513 | 539 | 481 | 0
299 | SACOI3 | TOOT | 94 | 104 | 82 | 28 | 31 | 24 | 41 | 42 | 40 | -230 | -192 | -253 | 8 | 34 | 86 | 881 | 889 | 868 | 0
309 | NeuConnect | TOOT | 254 | 266 | 235 | 54 | 57 | 50 | 117 | 125 | 107 | -438 | -405 | -466 | 14 | 64 | 164 | 2519 | 2666 | 2352 | 0
312 | St. Peter (AT) - Tauern (AT) | TOOT | 244 | 252 | 233 | 61 | 66 | 57 | 131 | 132 | 130 | -498 | -464 | -538 | 16 | 73 | 187 | 2788 | 2874 | 2751 | 0
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | TOOT | 245 | 252 | 233 | 62 | 67 | 57 | 130 | 132 | 127 | -508 | -464 | -546 | 17 | 74 | 190 | 2754 | 2874 | 2622 | 0
323 | Dekani (SI) - Zaule (IT) interconnection | TOOT | 5 | 10 | 1 | 2 | 2 | 0 | 3 | 5 | 2 | -12 | 7 | -20 | 0 | 2 | 5 | 65 | 117 | 37 | 0
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | TOOT | 2 | 4 | 0 | -1 | 2 | -6 | 2 | 3 | 0 | 7 | 49 | -13 | 0 | 0 | 0 | 32 | 68 | 8 | 0
325 | Obersielach (AT) - Podlog (SI) | PINT | 43 | 53 | 32 | 6 | 16 | 2 | 26 | 31 | 21 | -54 | -16 | -131 | 2 | 8 | 20 | 586 | 652 | 534 | 0
328 | Interconnector DE-LUX | TOOT | 5 | 10 | 1 | 1 | 2 | 0 | 3 | 5 | 2 | -10 | -4 | -20 | 0 | 1 | 4 | 66 | 102 | 34 | 0
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
330 | 4th 400kV CZ-SK interconnector | light PINT | 27 | 32 | 22 | 6 | 7 | 4 | 18 | 25 | 13 | -46 | -36 | -54 | 2 | 7 | 17 | 389 | 520 | 287 | 0
333 | PST Foretaille | PINT | 114 | 115 | 112 | 27 | 29 | 25 | 59 | 63 | 52 | -217 | -207 | -233 | 7 | 32 | 81 | 1260 | 1330 | 1136 | 0
335 | North Sea Wind Power Hub | light PINT | 258 | 287 | 240 | 289 | 297 | 278 | 1624 | 1632 | 1610 | -2351 | -2261 | -2416 | 78 | 343 | 882 | 34082 | 34419 | 33690 | 12000
338 | Adriatic HVDC link | PINT | 147 | 181 | 119 | 38 | 40 | 37 | 81 | 81 | 80 | -285 | -232 | -322 | 10 | 45 | 117 | 1380 | 1395 | 1366 | 0
339 | Tyrrhenian link | PINT | 124 | 133 | 111 | 18 | 20 | 16 | 110 | 123 | 99 | -181 | -157 | -229 | 5 | 22 | 56 | 2182 | 2295 | 2076 | 0
340 | Avelgem-Courcelles (Boucle du Hainaut): new corridor | TOOT
341 | North CSE Corridor | PINT | 48 | 53 | 39 | 7 | 12 | 0 | 40 | 47 | 35 | -55 | -3 | -94 | 2 | 8 | 21 | 798 | 869 | 743 | 0
342 | Central Balkan Corridor | PINT | 51 | 55 | 49 | 7 | 9 | 5 | 45 | 50 | 40 | -60 | -38 | -75 | 2 | 9 | 23 | 968 | 1055 | 849 | 0
343 | CSE1 New | PINT | 5 | 8 | 3 | 1 | 3 | -2 | 2 | 3 | 2 | -9 | 18 | -27 | 0 | 1 | 4 | 51 | 60 | 37 | 0
346 | ZuidWest380 NL Oost | PINT | 34 | 38 | 32 | 7 | 8 | 4 | 24 | 25 | 23 | -56 | -30 | -69 | 2 | 8 | 21 | 513 | 539 | 481 | 0
349 | MaresConnect | PINT | 142 | 152 | 132 | 37 | 38 | 36 | 63 | 65 | 61 | -301 | -290 | -308 | 10 | 44 | 113 | 1357 | 1400 | 1281 | 0
350 | South Balkan Corridor | TOOT | 31 | 35 | 27 | 6 | 10 | 4 | 24 | 26 | 21 | -51 | -35 | -81 | 2 | 8 | 19 | 496 | 548 | 439 | 0
375 | Lienz (AT) - Veneto region (IT) 220 kV | PINT | 109 | 130 | 88 | 22 | 32 | 8 | 53 | 59 | 48 | -191 | -108 | -257 | 6 | 26 | 67 | 994 | 1292 | 778 | 0
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | light PINT | 6 | 11 | 1 | 1 | 3 | -2 | 5 | 6 | 4 | -6 | 15 | -23 | 0 | 1 | 2 | 105 | 122 | 89 | 0
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | PINT | 35 | 38 | 33 | 8 | 8 | 6 | 23 | 23 | 23 | -61 | -48 | -69 | 2 | 9 | 23 | 499 | 519 | 481 | 0
378 | Transformer Gatica | TOOT
379 | Uprate Gatica lines | TOOT
1034 | HVDC corridor from Northern Germany to Western Germany | PINT | 7513 | 7513 | 7513 | 105 | 105 | 105 | 1422 | 1422 | 1422 | -3749 | -3749 | -3749 | 53 | 235 | 604 | 14224 | 14224 | 14224 | 0
1039 | SE North-south long-term reinforcements | light PINT | 25 | 29 | 20 | 6 | 9 | 4 | 10 | 15 | 8 | -49 | -36 | -77 | 2 | 7 | 19 | 223 | 312 | 170 | 0
1040 | LirIC | PINT | 95 | 103 | 89 | 26 | 29 | 24 | 36 | 38 | 35 | -215 | -191 | -232 | 7 | 31 | 81 | 779 | 819 | 741 | 0
1041 | GREGY Green Energy Interconnector | PINT | 1167 | 1186 | 1157 | 463 | 465 | 461 | 437 | 458 | 425 | -3767 | -3747 | -3780 | 124 | 550 | 1412 | 9401 | 10099 | 9046 | 0
1042 | Offshore Wind LT 1 | PINT | 28 | 31 | 23 | 1 | 3 | 0 | 35 | 42 | 31 | -9 | 4 | -27 | 0 | 1 | 3 | 761 | 875 | 632 | 700
1046 | Finnish North-South reinforcement | PINT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1047 | Emden-Eemshaven | light PINT | 85 | 85 | 85 | 16 | 18 | 15 | 51 | 55 | 47 | -133 | -121 | -146 | 4 | 19 | 50 | 1090 | 1172 | 1031 | 0
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | PINT | 967 | 985 | 951 | 319 | 330 | 313 | 477 | 489 | 468 | -2594 | -2541 | -2679 | 86 | 379 | 973 | 10190 | 10322 | 9962 | 0
1049 | Cronos Energy Ltd | PINT | 126 | 136 | 112 | 19 | 19 | 18 | 63 | 65 | 60 | -152 | -148 | -156 | 5 | 22 | 57 | 1358 | 1410 | 1288 | 0
1050 | Tarchon Energy Ltd | PINT | 245 | 247 | 243 | 46 | 50 | 42 | 105 | 110 | 98 | -377 | -343 | -405 | 12 | 55 | 141 | 2263 | 2326 | 2153 | 0
1051 | Aminth Energy Ltd | PINT | 260 | 263 | 257 | 53 | 54 | 52 | 114 | 119 | 105 | -432 | -426 | -436 | 14 | 63 | 162 | 2446 | 2524 | 2307 | 0
1052 | Lienz (AT) - Obersielach (AT) | PINT | 56 | 61 | 52 | 9 | 13 | 6 | 42 | 49 | 34 | -70 | -52 | -104 | 2 | 10 | 26 | 903 | 1025 | 755 | 0
1054 | Westtirol (AT) - Zell/Ziller (AT) | PINT | 68 | 71 | 67 | 18 | 20 | 17 | 36 | 39 | 33 | -149 | -137 | -165 | 5 | 22 | 56 | 752 | 825 | 680 | 0
1055 | Interconnection of Crete to the Mainland System of Greece | TOOT | 198 | 204 | 189 | 46 | 48 | 43 | 130 | 141 | 117 | -373 | -348 | -394 | 12 | 54 | 140 | 2789 | 2998 | 2566 | 0
1058 | HVDC Interconnector DE-CH | light PINT | 142 | 143 | 142 | 31 | 33 | 26 | 74 | 78 | 70 | -250 | -210 | -272 | 8 | 37 | 94 | 1600 | 1659 | 1549 | 0
1059 | Southern Italy | PINT | 8 | 10 | 5 | 0 | 1 | -1 | 9 | 12 | 6 | 0 | 11 | -7 | 0 | 0 | 0 | 181 | 245 | 137 | 0
1066 | Bulgaria - Turkey | light PINT | 449 | 472 | 433 | 186 | 188 | 183 | 139 | 153 | 126 | -1510 | -1489 | -1532 | 50 | 221 | 566 | 2989 | 3375 | 2685 | 0
1067 | New AC 400 kV interconnection line Greece - Turkey | light PINT | 285 | 287 | 283 | 112 | 122 | 101 | 95 | 102 | 87 | -910 | -825 | -991 | 30 | 133 | 341 | 2036 | 2251 | 1849 | 0
1068 | LaSGo Link | light PINT | 49 | 60 | 42 | 5 | 13 | 1 | 32 | 33 | 30 | -41 | -6 | -104 | 1 | 6 | 15 | 687 | 702 | 659 | 0
1074 | Pannonian Corridor | PINT | 19 | 20 | 18 | 6 | 8 | 5 | 12 | 15 | 10 | -46 | -38 | -61 | 2 | 7 | 17 | 258 | 331 | 219 | 0
1082 | Sea-Socket | light PINT | 80 | 82 | 79 | 10 | 11 | 9 | 71 | 74 | 69 | -82 | -73 | -87 | 3 | 12 | 31 | 1520 | 1555 | 1494 | 700
1085 | Malta-Italy Cable Link No.2 | PINT | 24 | 31 | 15 | 12 | 13 | 9 | 5 | 7 | 2 | -94 | -77 | -108 | 3 | 14 | 35 | 107 | 149 | 52 | 0
1086 | Estonia internal grid reinforcement to increase RES connection capability (RRF project) | PINT | 34 | 38 | 29 | 1 | 2 | 0 | 35 | 38 | 29 | -10 | -2 | -19 | 0 | 1 | 4 | 742 | 820 | 618 | 700
1088 | Latvia and Estonia Hybrid Off-Shore interconnector | PINT | 0 | 0 | 0 | 1 | 2 | 1 | 60 | 63 | 56 | -11 | -9 | -12 | 0 | 2 | 4 | 1250 | 1335 | 1190 | 1000
1092 | Triton Link: offshore hybrid HVDC interconnector Belgium – Denmark | PINT | 346 | 348 | 344 | 91 | 94 | 86 | 422 | 429 | 413 | -738 | -697 | -766 | 24 | 108 | 277 | 8853 | 8932 | 8756 | 3000
1094 | Estlink 3 | light PINT | 39 | 42 | 37 | 3 | 5 | 2 | 32 | 37 | 29 | -28 | -17 | -42 | 1 | 4 | 10 | 682 | 774 | 619 | 0
1095 | Aurora line 2 (4th AC Finland-Sweden north) | light PINT | 86 | 96 | 75 | -2 | 1 | -6 | 59 | 62 | 57 | 14 | 46 | -12 | 0 | 0 | 0 | 1286 | 1328 | 1245 | 0
1096 | Beznau - Mettlen | PINT | 81 | 93 | 69 | 15 | 23 | 6 | 56 | 61 | 49 | -125 | -50 | -188 | 4 | 18 | 47 | 1186 | 1283 | 1084 | 0
1097 | Upgrade to Konti-Skan | PINT | 78 | 95 | 63 | 12 | 18 | 7 | 44 | 44 | 44 | -96 | -58 | -145 | 3 | 14 | 36 | 945 | 964 | 926 | 0
1098 | Offshore Wind LT 2 | PINT | 30 | 36 | 23 | 1 | 3 | 0 | 34 | 41 | 31 | -11 | 4 | -27 | 0 | 2 | 4 | 734 | 865 | 653 | 700
1100 | Reinforcement of the existing CZ-DE interconnector (Hradec - Röhrsdorf) on the CZ side | PINT | 29 | 32 | 26 | 2 | 3 | -1 | 30 | 38 | 22 | -15 | 6 | -28 | 0 | 2 | 6 | 652 | 815 | 496 | 0
1102 | Mettlen - Ulrichen | light PINT | 23 | 25 | 18 | 4 | 6 | 1 | 16 | 17 | 14 | -32 | -7 | -51 | 1 | 5 | 12 | 342 | 366 | 303 | 0
1103 | Bickigen - Chippis | PINT | 57 | 66 | 52 | 12 | 16 | 9 | 37 | 41 | 36 | -96 | -77 | -134 | 3 | 14 | 36 | 800 | 837 | 774 | 0
1104 | Niederstedem - Roost | PINT | 2 | 7 | 0 | 1 | 3 | -1 | 1 | 2 | 0 | -7 | 5 | -25 | 0 | 1 | 2 | 17 | 47 | 0 | 0
1105 | Georgia-Romania Black Sea (submarine) interconnection cable project | PINT | 241 | 243 | 238 | 18 | 21 | 16 | 225 | 249 | 201 | -199 | -130 | -268 | 5 | 22 | 56 | 5468 | 5642 | 5295 | 0
1106 | Bornholm Energy Island (BEI) | TOOT | 94 | 127 | 72 | 38 | 43 | 30 | 245 | 285 | 223 | -309 | -245 | -347 | 10 | 45 | 116 | 5143 | 6068 | 4657 | 2000
1107 | EuroAfrica Interconnector | PINT | 90 | 90 | 89 | 29 | 31 | 26 | 31 | 34 | 27 | -235 | -213 | -253 | 8 | 34 | 88 | 661 | 759 | 566 | 0
1109 | Basilicata - Campania reinforcements | PINT | 12 | 14 | 8 | 0 | 1 | -2 | 16 | 20 | 12 | 2 | 18 | -10 | 0 | 0 | 0 | 305 | 331 | 270 | 0
1110 | Sicily - Calabria | PINT | 3 | 5 | 0 | -1 | 0 | -3 | 5 | 6 | 4 | 9 | 28 | 0 | 0 | 0 | 0 | 107 | 130 | 75 | 0
1112 | GRITA 2 | PINT | 61 | 78 | 42 | 10 | 15 | 5 | 40 | 49 | 33 | -92 | -62 | -125 | 3 | 12 | 31 | 801 | 909 | 718 | 0
1119 | Bisamberg (AT) - Wien SO (AT) - Parndorf (AT) | PINT | 140 | 140 | 140 | 28 | 28 | 28 | 150 | 150 | 150 | -228 | -228 | -228 | 8 | 33 | 85 | 3166 | 3166 | 3166 | 3000
1120 | Wien SO (AT) – Ternitz (AT) – Hessenberg (AT) | PINT | 40 | 40 | 40 | 8 | 8 | 8 | 31 | 31 | 31 | -62 | -62 | -62 | 2 | 9 | 23 | 663 | 663 | 663 | 750
1121 | Hessenberg (AT) - Weißenbach (AT) | PINT | 27 | 27 | 27 | 3 | 3 | 3 | 30 | 30 | 30 | -24 | -24 | -24 | 1 | 4 | 9 | 632 | 632 | 632 | 600
1122 | Offshore Wind connection Centre Manche 1 | TOOT | 138 | 142 | 134 | 15 | 21 | 12 | 158 | 163 | 150 | -124 | -99 | -167 | 4 | 18 | 46 | 3382 | 3445 | 3311 | 1250
1123 | Offshore Wind Connection Centre Manche 2 | PINT | 138 | 142 | 134 | 15 | 21 | 12 | 158 | 163 | 150 | -124 | -99 | -167 | 4 | 18 | 46 | 3382 | 3445 | 3311 | 1250
1124 | Offshore Wind Connection South Britanny | TOOT | 84 | 88 | 81 | 9 | 10 | 7 | 95 | 98 | 90 | -72 | -58 | -84 | 2 | 11 | 27 | 2032 | 2063 | 1978 | 750
1125 | Offshore Wind Connection Occitanie | TOOT | 84 | 88 | 81 | 9 | 10 | 7 | 95 | 98 | 90 | -72 | -58 | -84 | 2 | 11 | 27 | 2032 | 2063 | 1978 | 750
1126 | Offshore Wind Connection PACA | TOOT | 84 | 88 | 81 | 9 | 10 | 7 | 95 | 98 | 90 | -72 | -58 | -84 | 2 | 11 | 27 | 2032 | 2063 | 1978 | 750
1127 | Offshore Wind Connection South Atlantic | PINT | 139 | 142 | 137 | 15 | 21 | 12 | 158 | 163 | 150 | -124 | -99 | -167 | 4 | 18 | 47 | 3383 | 3449 | 3311 | 1250
1129 | New RES at Minho region | TOOT | 23 | 30 | 20 | 1 | 4 | -1 | 21 | 25 | 18 | -11 | 10 | -32 | 0 | 2 | 4 | 458 | 523 | 406 | 400

## 2030DEGS
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_market_SEW |  |  | ΔRES |  |  | ΔRES_MW
|  |  | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | low | mid | high | weighted avg | max | min | Explicit
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW
1 | RES in north of Portugal | TOOT | 106 | 107 | 105 | 28 | 35 | 21 | 73 | 75 | 70 | -360 | -271 | -445 | 0 | 8 | 40 | 934 | 978 | 889 | 1154
4 | Interconnection Portugal-Spain | TOOT | 35 | 47 | 25 | 9 | 13 | 6 | 19 | 28 | 9 | -118 | -75 | -168 | 0 | 3 | 13 | 240 | 359 | 116 | 0
16 | Biscay Gulf | TOOT | 516 | 518 | 515 | 118 | 129 | 104 | 411 | 432 | 393 | -1516 | -1338 | -1649 | 0 | 33 | 168 | 5303 | 5463 | 5122 | 0
26 | Reschenpass Interconnector Project | TOOT | 36 | 42 | 33 | 14 | 17 | 12 | 8 | 13 | 4 | -179 | -152 | -221 | 0 | 4 | 20 | 97 | 167 | 57 | 0
28 | Italy-Montenegro | PINT | 51 | 53 | 48 | 17 | 24 | 13 | 26 | 34 | 21 | -232 | -161 | -313 | 0 | 5 | 25 | 340 | 436 | 273 | 0
29 | Italy-Tunisia | TOOT | 195 | 219 | 163 | 55 | 57 | 54 | 66 | 74 | 56 | -727 | -688 | -765 | 0 | 15 | 78 | 846 | 936 | 720 | 0
33 | Central Northern Italy | TOOT | 34 | 47 | 18 | 15 | 17 | 12 | 24 | 32 | 16 | -193 | -170 | -220 | 0 | 4 | 21 | 309 | 403 | 212 | 0
35 | CZ Southwest-east corridor | PINT | 47 | 52 | 37 | 9 | 15 | 5 | 8 | 12 | 6 | -114 | -64 | -196 | 0 | 3 | 13 | 119 | 156 | 76 | 0
40 | Belgium-Luxembourg-Germany: long-term perspective | light PINT | 43 | 50 | 34 | 10 | 12 | 8 | 8 | 10 | 6 | -128 | -104 | -153 | 0 | 3 | 14 | 115 | 135 | 99 | 0
47 | Westtirol (AT) - Vöhringen (DE) | PINT | 65 | 75 | 58 | 18 | 26 | 11 | 5 | 6 | 4 | -244 | -145 | -368 | 0 | 5 | 26 | 95 | 224 | 49 | 0
81 | North South Interconnector | TOOT | 74 | 90 | 56 | 20 | 22 | 17 | 29 | 36 | 21 | -255 | -217 | -284 | 0 | 6 | 28 | 371 | 467 | 276 | 0
85 | Integration of RES in Alentejo | TOOT | 19 | 23 | 13 | 4 | 7 | 0 | 39 | 42 | 37 | -50 | -5 | -88 | 0 | 1 | 6 | 505 | 545 | 480 | 700
94 | GerPol Improvements | TOOT | 227 | 230 | 225 | 42 | 46 | 38 | 62 | 71 | 54 | -537 | -490 | -584 | 0 | 12 | 60 | 796 | 892 | 700 | 0
103 | Reinforcements Ring NL phase I | TOOT | 49 | 52 | 46 | 8 | 10 | 6 | 11 | 16 | 4 | -102 | -80 | -133 | 0 | 2 | 11 | 153 | 199 | 52 | 0
107 | Celtic Interconnector | TOOT | 263 | 275 | 245 | 60 | 65 | 51 | 145 | 147 | 143 | -766 | -660 | -837 | 0 | 17 | 85 | 1873 | 1914 | 1815 | 0
111 | Aurora line (3rd AC Finland-Sweden north) | TOOT | 84 | 88 | 78 | 7 | 8 | 5 | 74 | 74 | 74 | -85 | -68 | -103 | 0 | 2 | 9 | 1150 | 1275 | 967 | 0
120 | Belgian Modular Offshore Grid II (MOG II) | TOOT | 1043 | 1051 | 1033 | 258 | 264 | 252 | 1136 | 1161 | 1110 | -3313 | -3230 | -3390 | 0 | 73 | 368 | 14639 | 14717 | 14514 | 3500
121 | Nautilus: multi-purpose interconnector Belgium - UK | PINT | 341 | 457 | 225 | 75 | 110 | 40 | 36 | 40 | 31 | -962 | -513 | -1411 | 0 | 21 | 107 | 459 | 528 | 390 | 0
123 | LitPol Link Stage 2 | TOOT | 219 | 234 | 201 | 148 | 156 | 138 | 62 | 75 | 48 | -1900 | -1774 | -1999 | 0 | 42 | 211 | 871 | 979 | 809 | 0
124 | NordBalt phase 2 | PINT | 57 | 65 | 50 | 15 | 17 | 12 | 32 | 37 | 23 | -186 | -158 | -213 | 0 | 4 | 21 | 445 | 483 | 400 | 0
126 | SE North-south short-term reinforcements | TOOT | 159 | 169 | 150 | 25 | 29 | 21 | 62 | 69 | 55 | -321 | -273 | -370 | 0 | 7 | 36 | 920 | 952 | 888 | 0
127 | Central Southern Italy | TOOT | 43 | 58 | 24 | 18 | 24 | 8 | 67 | 71 | 60 | -233 | -108 | -309 | 0 | 5 | 25 | 807 | 914 | 648 | 0
130 | HVDC SuedOstLink Wolmirstedt to area Isar | TOOT | 2174 | 2174 | 2174 | 41 | 41 | 41 | 371 | 371 | 371 | -1478 | -1478 | -1478 | 0 | 33 | 164 | 3718 | 3718 | 3718 | 0
132 | HVDC Line A-North | TOOT | 5249 | 5249 | 5249 | 129 | 129 | 129 | 853 | 853 | 853 | -4603 | -4603 | -4603 | 0 | 101 | 511 | 8531 | 8531 | 8531 | 0
138 | Black Sea Corridor | TOOT | 76 | 78 | 73 | 38 | 40 | 37 | 26 | 35 | 18 | -489 | -474 | -509 | 0 | 11 | 54 | 362 | 446 | 306 | 0
142 | CSE4 | TOOT | 17 | 23 | 12 | -19 | -15 | -23 | 13 | 15 | 10 | 245 | 294 | 191 | 4 | 0 | 0 | 178 | 199 | 166 | 0
144 | Mid Continental East corridor | TOOT | 156 | 157 | 154 | 88 | 104 | 69 | 78 | 80 | 75 | -1128 | -885 | -1328 | 0 | 25 | 125 | 1004 | 1045 | 982 | 0
150 | Italy-Slovenia | light PINT | 80 | 83 | 76 | -4 | 2 | -12 | 15 | 21 | 12 | 50 | 158 | -31 | 1 | 0 | 0 | 192 | 272 | 154 | 0
153 | France-Alderney-Britain | PINT | 423 | 424 | 422 | 81 | 96 | 60 | 46 | 48 | 43 | -1038 | -764 | -1232 | 0 | 23 | 115 | 596 | 633 | 560 | 0
170 | Baltic States Synchronization with Continental Europe | TOOT | 303 | 326 | 283 | 207 | 221 | 193 | 91 | 93 | 89 | -2655 | -2475 | -2829 | 0 | 58 | 295 | 1265 | 1461 | 1157 | 0
174 | Greenconnector | PINT | 86 | 110 | 50 | 14 | 23 | 8 | 7 | 9 | 4 | -183 | -110 | -297 | 0 | 4 | 20 | 89 | 120 | 52 | 0
176 | Hansa PowerBridge I | TOOT | 343 | 348 | 338 | 145 | 146 | 144 | 76 | 83 | 70 | -1857 | -1845 | -1868 | 0 | 41 | 206 | 1123 | 1197 | 1049 | 0
183 | DKW-DE, Westcoast | TOOT | 287 | 288 | 286 | 133 | 135 | 131 | 135 | 149 | 121 | -1703 | -1674 | -1731 | 0 | 37 | 189 | 1986 | 2082 | 1890 | 0
186 | East of Austria | TOOT | 429 | 438 | 421 | 143 | 146 | 141 | 448 | 454 | 439 | -1767 | -1413 | -2086 | 0 | 40 | 204 | 5824 | 5896 | 5742 | 2000
187 | St. Peter (AT) - Pleinting (DE) | PINT | 141 | 148 | 134 | 41 | 52 | 27 | 9 | 13 | 7 | -539 | -342 | -742 | 0 | 12 | 58 | 162 | 289 | 91 | 0
190 | NorthConnect | TOOT | 852 | 882 | 794 | 204 | 238 | 150 | 124 | 192 | 61 | -2615 | -1925 | -3056 | 0 | 58 | 290 | 1692 | 2532 | 780 | 0
200 | CZ Northwest-South corridor | TOOT | 62 | 63 | 61 | 14 | 21 | 3 | 11 | 14 | 8 | -175 | -44 | -264 | 0 | 4 | 19 | 150 | 186 | 132 | 0
210 | Würmlach (AT) - Somplago (IT) interconnection | TOOT | 16 | 25 | 4 | 7 | 12 | 0 | 2 | 4 | 1 | -90 | 4 | -159 | 0 | 2 | 10 | 24 | 48 | 7 | 0
219 | EuroAsia Interconnector | TOOT | 656 | 676 | 636 | 142 | 151 | 134 | 421 | 435 | 408 | -1825 | -1717 | -1933 | 0 | 40 | 203 | 5414 | 5501 | 5328 | 0
225 | 2nd interconnector Belgium - Germany | light PINT | 84 | 90 | 79 | 12 | 17 | 7 | 17 | 20 | 11 | -148 | -84 | -213 | 0 | 3 | 16 | 232 | 267 | 182 | 0
227 | Transbalkan Corridor | TOOT | 46 | 50 | 42 | -1 | 6 | -9 | 26 | 42 | 16 | 13 | 121 | -81 | 0 | 0 | 0 | 357 | 547 | 229 | 0
228 | Muhlbach - Eichstetten | TOOT | 63 | 66 | 60 | 21 | 27 | 16 | 6 | 9 | 5 | -276 | -209 | -344 | 0 | 6 | 31 | 88 | 116 | 63 | 0
230 | GerPol Power Bridge I | TOOT | 289 | 290 | 287 | 199 | 200 | 197 | 35 | 46 | 27 | -2545 | -2520 | -2566 | 0 | 56 | 283 | 492 | 579 | 435 | 0
231 | Beznau - Tiengen | PINT | 54 | 57 | 50 | 16 | 20 | 8 | 9 | 11 | 6 | -199 | -103 | -257 | 0 | 4 | 22 | 124 | 138 | 102 | 0
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Bergrheinfeld West | TOOT | 9783 | 9783 | 9783 | 248 | 248 | 248 | 1668 | 1668 | 1668 | -8869 | -8869 | -8869 | 0 | 195 | 984 | 16684 | 16684 | 16684 | 0
239 | Fenno-Skan 1 renewal | light PINT | 36 | 44 | 31 | 3 | 3 | 3 | 40 | 51 | 28 | -37 | -33 | -41 | 0 | 1 | 4 | 549 | 668 | 478 | 0
243 | New 400 kV interconnection line between Serbia and Croatia | light PINT | 14 | 18 | 11 | 5 | 11 | -1 | 3 | 7 | 0 | -64 | 11 | -136 | 0 | 1 | 7 | 36 | 84 | 1 | 0
244 | Vigy - Uchtelfangen area | PINT | 281 | 294 | 268 | 98 | 107 | 90 | 32 | 39 | 24 | -1259 | -1154 | -1374 | 0 | 28 | 140 | 444 | 512 | 392 | 0
247 | AQUIND Interconnector | PINT | 601 | 608 | 594 | 135 | 138 | 129 | 43 | 60 | 29 | -1730 | -1654 | -1772 | 0 | 38 | 192 | 557 | 775 | 367 | 0
250 | Merchant line Castasegna (CH) - Mese (IT) | PINT | 17 | 19 | 11 | 1 | 6 | -3 | 2 | 4 | 1 | -16 | 42 | -83 | 0 | 0 | 2 | 27 | 47 | 14 | 0
252 | Internal Belgian Backbone Center-East: HTLS upgrade Massenhoven-VanEyck-Gramme-Courcelles-Bruegel-Mercator | PINT
253 | Upstream reinforcement in France to increase FR-CH capacity | PINT | 48 | 55 | 40 | 13 | 18 | 9 | 4 | 5 | 3 | -162 | -117 | -233 | 0 | 4 | 18 | 50 | 62 | 36 | 0
254 | HVDC Ultranet Osterath to Philippsburg | TOOT | 1683 | 1683 | 1683 | 38 | 38 | 38 | 300 | 300 | 300 | -1366 | -1366 | -1366 | 0 | 30 | 152 | 2996 | 2996 | 2996 | 0
259 | HU-RO | PINT | 66 | 68 | 62 | 27 | 31 | 21 | 28 | 32 | 22 | -342 | -265 | -393 | 0 | 8 | 38 | 393 | 415 | 379 | 0
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | PINT | 221 | 270 | 171 | 38 | 39 | 37 | 31 | 33 | 28 | -485 | -474 | -496 | 0 | 11 | 54 | 397 | 424 | 371 | 2000
263 | Lake Constance East | light PINT | 158 | 168 | 148 | 40 | 45 | 33 | 16 | 21 | 13 | -509 | -429 | -573 | 0 | 11 | 56 | 212 | 274 | 172 | 0
267 | Hansa PowerBridge II | light PINT | 310 | 315 | 306 | 131 | 131 | 130 | 64 | 68 | 60 | -1676 | -1670 | -1683 | 0 | 37 | 186 | 949 | 1038 | 860 | 0
270 | FR-ES project -Aragón-Atlantic Pyrenees | PINT | 266 | 272 | 259 | 68 | 71 | 64 | 237 | 241 | 228 | -866 | -817 | -914 | 0 | 19 | 96 | 3064 | 3123 | 2969 | 0
276 | FR-ES project -Navarra-Landes | PINT | 266 | 272 | 259 | 68 | 71 | 64 | 237 | 241 | 228 | -866 | -817 | -914 | 0 | 19 | 96 | 3064 | 3123 | 2969 | 0
280 | FR-BE: study Lonny-Achene-Gramme | PINT | 146 | 149 | 144 | 46 | 52 | 38 | 9 | 11 | 6 | -588 | -487 | -670 | 0 | 13 | 65 | 113 | 143 | 80 | 0
283 | TuNur Italy | PINT | 1057 | 1276 | 864 | 269 | 311 | 233 | 883 | 972 | 810 | -3552 | -2985 | -4168 | 0 | 76 | 382 | 11378 | 12592 | 10578 | 4900
285 | GridLink | PINT | 426 | 428 | 424 | 94 | 96 | 92 | 36 | 43 | 29 | -1208 | -1185 | -1232 | 0 | 27 | 134 | 464 | 560 | 369 | 0
286 | Greenlink | PINT | 155 | 156 | 154 | 28 | 30 | 27 | 87 | 94 | 77 | -364 | -341 | -381 | 0 | 8 | 40 | 1292 | 1435 | 1197 | 0
293 | Southern Aegean Interconnector | PINT | 92 | 95 | 89 | 29 | 30 | 27 | 78 | 91 | 65 | -371 | -348 | -382 | 0 | 8 | 41 | 1102 | 1177 | 1017 | 582
297 | BRABO II + III | TOOT | 44 | 45 | 44 | 8 | 13 | 5 | 29 | 36 | 24 | -108 | -61 | -170 | 0 | 2 | 12 | 376 | 453 | 312 | 0
299 | SACOI3 | TOOT | 127 | 140 | 113 | 31 | 36 | 26 | 76 | 87 | 68 | -394 | -329 | -466 | 0 | 9 | 44 | 982 | 1101 | 889 | 0
309 | NeuConnect | TOOT | 404 | 437 | 360 | 71 | 84 | 56 | 39 | 49 | 25 | -941 | -714 | -1194 | 0 | 20 | 101 | 503 | 645 | 318 | 0
312 | St. Peter (AT) - Tauern (AT) | TOOT | 253 | 266 | 232 | 80 | 90 | 69 | 28 | 37 | 19 | -1062 | -887 | -1265 | 0 | 23 | 114 | 357 | 468 | 245 | 0
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | TOOT | 255 | 272 | 232 | 86 | 92 | 73 | 21 | 24 | 19 | -1136 | -942 | -1265 | 0 | 24 | 122 | 347 | 468 | 245 | 0
323 | Dekani (SI) - Zaule (IT) interconnection | TOOT | 2 | 5 | 0 | 1 | 5 | -3 | 2 | 6 | 0 | -18 | 40 | -70 | 0 | 0 | 2 | 22 | 79 | 0 | 0
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | TOOT | 3 | 4 | 0 | -1 | 0 | -2 | 4 | 11 | 0 | 11 | 20 | -2 | 0 | 0 | 0 | 55 | 137 | 0 | 0
325 | Obersielach (AT) - Podlog (SI) | PINT | 40 | 45 | 37 | 15 | 20 | 11 | 4 | 8 | 2 | -192 | -155 | -256 | 0 | 4 | 21 | 60 | 111 | 32 | 0
328 | Interconnector DE-LUX | TOOT | 10 | 14 | 4 | -2 | 2 | -6 | 4 | 13 | 1 | 21 | 83 | -30 | 0 | 0 | 0 | 52 | 159 | 14 | 0
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
330 | 4th 400kV CZ-SK interconnector | light PINT | 20 | 24 | 17 | 10 | 11 | 10 | 1 | 2 | 0 | -134 | -133 | -136 | 0 | 3 | 15 | 16 | 25 | 5 | 0
333 | PST Foretaille | PINT | 163 | 179 | 154 | 61 | 68 | 49 | 17 | 23 | 12 | -809 | -702 | -874 | 0 | 18 | 87 | 215 | 292 | 147 | 0
335 | North Sea Wind Power Hub | light PINT | 1798 | 1808 | 1788 | 1103 | 1123 | 1084 | 4410 | 4410 | 4410 | -14144 | -13894 | -14394 | 0 | 311 | 1570 | 55865 | 55885 | 55846 | 12000
338 | Adriatic HVDC link | PINT | 85 | 88 | 82 | 20 | 21 | 19 | 44 | 49 | 40 | -270 | -246 | -294 | 0 | 6 | 28 | 561 | 617 | 505 | 0
339 | Tyrrhenian link | PINT | 88 | 110 | 67 | 23 | 24 | 23 | 76 | 94 | 57 | -308 | -291 | -324 | 0 | 7 | 33 | 972 | 1192 | 727 | 0
340 | Avelgem-Courcelles (Boucle du Hainaut): new corridor | TOOT
341 | North CSE Corridor | PINT | 45 | 51 | 40 | 35 | 37 | 32 | 24 | 28 | 15 | -403 | -276 | -476 | 0 | 10 | 49 | 305 | 361 | 197 | 0
342 | Central Balkan Corridor | PINT | 30 | 32 | 27 | 9 | 14 | 3 | 12 | 17 | 8 | -112 | -42 | -175 | 0 | 2 | 12 | 157 | 229 | 106 | 0
343 | CSE1 New | PINT | 11 | 14 | 9 | 0 | 3 | -1 | 3 | 7 | 1 | -1 | 18 | -34 | 0 | 0 | 0 | 40 | 87 | 8 | 0
346 | ZuidWest380 NL Oost | PINT | 26 | 29 | 24 | -1 | 4 | -7 | 18 | 21 | 12 | 10 | 92 | -45 | 0 | 0 | 0 | 232 | 275 | 150 | 0
349 | MaresConnect | PINT | 221 | 226 | 216 | 41 | 42 | 39 | 135 | 145 | 124 | -526 | -503 | -538 | 0 | 12 | 58 | 1739 | 1841 | 1629 | 0
350 | South Balkan Corridor | TOOT | 25 | 28 | 20 | 5 | 7 | 3 | 10 | 12 | 8 | -66 | -45 | -89 | 0 | 1 | 7 | 140 | 150 | 123 | 0
375 | Lienz (AT) - Veneto region (IT) 220 kV | PINT | 62 | 74 | 46 | 12 | 16 | 8 | 9 | 15 | 3 | -158 | -118 | -200 | 0 | 3 | 17 | 110 | 182 | 34 | 0
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | light PINT | 5 | 8 | 3 | -2 | 1 | -4 | 5 | 11 | 0 | 28 | 57 | -8 | 0 | 0 | 0 | 62 | 141 | 5 | 0
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | PINT | 27 | 31 | 24 | 0 | 6 | -7 | 23 | 28 | 21 | 0 | 92 | -77 | 0 | 0 | 0 | 299 | 349 | 273 | 0
378 | Transformer Gatica | TOOT
379 | Uprate Gatica lines | TOOT
1034 | HVDC corridor from Northern Germany to Western Germany | PINT | 7224 | 7224 | 7224 | 170 | 170 | 170 | 1276 | 1276 | 1276 | -6081 | -6081 | -6081 | 0 | 134 | 675 | 12756 | 12756 | 12756 | 0
1039 | SE North-south long-term reinforcements | light PINT | 32 | 34 | 31 | 13 | 18 | 5 | 12 | 25 | 1 | -165 | -62 | -230 | 0 | 4 | 18 | 150 | 328 | 16 | 0
1040 | LirIC | PINT | 155 | 161 | 147 | 32 | 34 | 30 | 105 | 119 | 94 | -412 | -380 | -433 | 0 | 9 | 46 | 1355 | 1501 | 1225 | 0
1041 | GREGY Green Energy Interconnector | PINT | 505 | 547 | 482 | 87 | 129 | 30 | 91 | 134 | 44 | -1132 | -434 | -1660 | 0 | 25 | 124 | 1177 | 1751 | 564 | 0
1042 | Offshore Wind LT 1 | PINT | 58 | 67 | 53 | 6 | 16 | 0 | 112 | 138 | 79 | -84 | -3 | -200 | 0 | 2 | 9 | 1656 | 1738 | 1500 | 700
1046 | Finnish North-South reinforcement | PINT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1047 | Emden-Eemshaven | light PINT | 70 | 72 | 68 | 9 | 10 | 7 | 15 | 20 | 11 | -117 | -88 | -134 | 0 | 3 | 13 | 196 | 259 | 144 | 0
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | PINT | 999 | 1019 | 979 | 235 | 243 | 223 | 658 | 705 | 521 | -3008 | -2854 | -3120 | 0 | 66 | 334 | 9159 | 9205 | 9057 | 0
1049 | Cronos Energy Ltd | PINT | 277 | 281 | 273 | 51 | 61 | 40 | 30 | 40 | 21 | -650 | -513 | -783 | 0 | 14 | 72 | 391 | 528 | 261 | 0
1050 | Tarchon Energy Ltd | PINT | 350 | 356 | 344 | 57 | 63 | 54 | 33 | 37 | 27 | -735 | -697 | -804 | 0 | 16 | 82 | 432 | 482 | 345 | 0
1051 | Aminth Energy Ltd | PINT | 503 | 511 | 495 | 103 | 116 | 86 | 189 | 190 | 187 | -1320 | -1108 | -1489 | 0 | 29 | 147 | 2469 | 2488 | 2450 | 0
1052 | Lienz (AT) - Obersielach (AT) | PINT | 39 | 40 | 37 | 15 | 20 | 12 | 9 | 14 | 5 | -190 | -155 | -256 | 0 | 4 | 21 | 115 | 175 | 60 | 0
1054 | Westtirol (AT) - Zell/Ziller (AT) | PINT | 60 | 64 | 58 | 17 | 22 | 11 | 8 | 17 | 4 | -213 | -145 | -288 | 0 | 5 | 24 | 107 | 224 | 60 | 0
1055 | Interconnection of Crete to the Mainland System of Greece | TOOT | 418 | 421 | 416 | 118 | 133 | 100 | 344 | 359 | 329 | -1511 | -1284 | -1705 | 0 | 33 | 168 | 4433 | 4537 | 4290 | 0
1058 | HVDC Interconnector DE-CH | light PINT | 132 | 150 | 108 | 36 | 44 | 28 | 18 | 24 | 14 | -468 | -363 | -560 | 0 | 10 | 52 | 233 | 300 | 182 | 0
1059 | Southern Italy | PINT | 6 | 11 | 4 | 2 | 5 | -2 | 8 | 10 | 7 | -23 | 24 | -61 | 0 | 0 | 2 | 104 | 130 | 87 | 0
1066 | Bulgaria - Turkey | light PINT | 198 | 222 | 174 | 127 | 128 | 125 | 27 | 42 | 16 | -1622 | -1605 | -1640 | 0 | 36 | 180 | 351 | 554 | 211 | 0
1067 | New AC 400 kV interconnection line Greece - Turkey | light PINT | 120 | 121 | 120 | 50 | 68 | 37 | 33 | 38 | 27 | -637 | -475 | -877 | 0 | 14 | 71 | 424 | 502 | 350 | 0
1068 | LaSGo Link | light PINT | 58 | 63 | 55 | 14 | 17 | 9 | 25 | 33 | 15 | -173 | -110 | -213 | 0 | 4 | 19 | 352 | 435 | 268 | 0
1074 | Pannonian Corridor | PINT | 18 | 25 | 13 | 9 | 17 | 3 | 3 | 4 | 1 | -119 | -41 | -215 | 0 | 3 | 13 | 34 | 59 | 17 | 0
1082 | Sea-Socket | light PINT | 153 | 154 | 151 | 31 | 37 | 24 | 147 | 152 | 144 | -401 | -306 | -477 | 0 | 9 | 45 | 1900 | 1920 | 1873 | 700
1085 | Malta-Italy Cable Link No.2 | PINT | 14 | 16 | 12 | 1 | 3 | 0 | 1 | 2 | 1 | -15 | -4 | -35 | 0 | 0 | 2 | 15 | 20 | 12 | 0
1086 | Estonia internal grid reinforcement to increase RES connection capability (RRF project) | PINT | 59 | 67 | 54 | 10 | 15 | 5 | 105 | 128 | 85 | -124 | -65 | -190 | 0 | 3 | 14 | 1470 | 1612 | 1333 | 700
1088 | Latvia and Estonia Hybrid Off-Shore interconnector | PINT | 18 | 24 | 13 | 7 | 8 | 6 | 180 | 217 | 147 | -88 | -72 | -105 | 0 | 2 | 10 | 2528 | 2739 | 2310 | 1000
1092 | Triton Link: offshore hybrid HVDC interconnector Belgium – Denmark | PINT | 504 | 504 | 504 | 229 | 229 | 228 | 839 | 964 | 714 | -2934 | -2929 | -2939 | 0 | 65 | 326 | 12242 | 12276 | 12208 | 3000
1094 | Estlink 3 | light PINT | 73 | 86 | 64 | 24 | 28 | 21 | 48 | 49 | 47 | -306 | -264 | -362 | 0 | 7 | 34 | 587 | 636 | 526 | 0
1095 | Aurora line 2 (4th AC Finland-Sweden north) | light PINT | 57 | 65 | 50 | 6 | 8 | 3 | 63 | 65 | 61 | -71 | -32 | -107 | 0 | 2 | 8 | 808 | 822 | 800 | 0
1096 | Beznau - Mettlen | PINT | 61 | 75 | 46 | 19 | 21 | 18 | 10 | 14 | 7 | -249 | -225 | -272 | 0 | 5 | 28 | 139 | 173 | 114 | 0
1097 | Upgrade to Konti-Skan | PINT | 150 | 169 | 125 | 46 | 55 | 35 | 51 | 59 | 41 | -584 | -449 | -703 | 0 | 13 | 65 | 657 | 749 | 533 | 0
1098 | Offshore Wind LT 2 | PINT | 60 | 67 | 53 | 7 | 16 | 0 | 128 | 138 | 115 | -96 | -3 | -200 | 0 | 2 | 11 | 1649 | 1738 | 1500 | 700
1100 | Reinforcement of the existing CZ-DE interconnector (Hradec - Röhrsdorf) on the CZ side | PINT | 30 | 34 | 26 | 16 | 21 | 11 | 15 | 17 | 12 | -204 | -143 | -265 | 0 | 4 | 23 | 185 | 217 | 152 | 0
1102 | Mettlen - Ulrichen | light PINT | 19 | 24 | 15 | 5 | 6 | 5 | 4 | 6 | 2 | -68 | -59 | -82 | 0 | 2 | 8 | 51 | 82 | 35 | 0
1103 | Bickigen - Chippis | PINT | 42 | 45 | 40 | 15 | 19 | 10 | 6 | 9 | 5 | -186 | -122 | -241 | 0 | 4 | 21 | 88 | 118 | 61 | 0
1104 | Niederstedem - Roost | PINT | 2 | 4 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | -11 | 0 | -24 | 0 | 0 | 1 | 5 | 13 | 0 | 0
1105 | Georgia-Romania Black Sea (submarine) interconnection cable project | PINT | 212 | 216 | 209 | 35 | 43 | 26 | 42 | 44 | 40 | -454 | -337 | -551 | 0 | 10 | 50 | 461 | 573 | 299 | 0
1106 | Bornholm Energy Island (BEI) | TOOT | 345 | 372 | 305 | 231 | 248 | 211 | 626 | 637 | 614 | -2964 | -2700 | -3177 | 0 | 65 | 329 | 8076 | 8129 | 8029 | 2000
1107 | EuroAfrica Interconnector | PINT | 147 | 184 | 121 | 40 | 47 | 35 | 65 | 74 | 55 | -507 | -454 | -606 | 0 | 11 | 56 | 837 | 963 | 709 | 0
1109 | Basilicata - Campania reinforcements | PINT | 13 | 17 | 9 | 4 | 5 | 3 | 18 | 27 | 12 | -53 | -46 | -65 | 0 | 1 | 6 | 231 | 335 | 155 | 0
1110 | Sicily - Calabria | PINT | 8 | 11 | 5 | 2 | 5 | -1 | 5 | 11 | 1 | -24 | 16 | -59 | 0 | 0 | 3 | 61 | 136 | 7 | 0
1112 | GRITA 2 | PINT | 80 | 82 | 77 | 26 | 28 | 25 | 56 | 57 | 53 | -336 | -316 | -357 | 0 | 7 | 37 | 718 | 743 | 676 | 0
1119 | Bisamberg (AT) - Wien SO (AT) - Parndorf (AT) | PINT | 496 | 496 | 496 | 147 | 147 | 147 | 528 | 528 | 528 | -1879 | -1879 | -1879 | 0 | 41 | 209 | 6836 | 6836 | 6836 | 3000
1120 | Wien SO (AT) – Ternitz (AT) – Hessenberg (AT) | PINT | 139 | 139 | 139 | 36 | 36 | 36 | 132 | 132 | 132 | -457 | -457 | -457 | 0 | 10 | 51 | 1711 | 1711 | 1711 | 750
1121 | Hessenberg (AT) - Weißenbach (AT) | PINT | 114 | 114 | 114 | 33 | 33 | 33 | 95 | 95 | 95 | -429 | -429 | -429 | 0 | 9 | 48 | 1233 | 1233 | 1233 | 600
1122 | Offshore Wind connection Centre Manche 1 | TOOT | 288 | 294 | 279 | 62 | 71 | 54 | 385 | 387 | 383 | -794 | -692 | -915 | 0 | 17 | 88 | 5066 | 5146 | 5007 | 1250
1123 | Offshore Wind Connection Centre Manche 2 | PINT | 292 | 294 | 290 | 66 | 71 | 60 | 397 | 406 | 387 | -845 | -775 | -915 | 0 | 19 | 94 | 5095 | 5146 | 5043 | 1250
1124 | Offshore Wind Connection South Britanny | TOOT | 173 | 177 | 167 | 33 | 40 | 23 | 234 | 238 | 232 | -424 | -290 | -519 | 0 | 9 | 47 | 3027 | 3034 | 3013 | 750
1125 | Offshore Wind Connection Occitanie | TOOT | 173 | 177 | 167 | 33 | 40 | 23 | 234 | 238 | 232 | -424 | -290 | -519 | 0 | 9 | 47 | 3027 | 3034 | 3013 | 750
1126 | Offshore Wind Connection PACA | TOOT | 173 | 177 | 167 | 33 | 40 | 23 | 234 | 238 | 232 | -424 | -290 | -519 | 0 | 9 | 47 | 3027 | 3034 | 3013 | 750
1127 | Offshore Wind Connection South Atlantic | PINT | 286 | 295 | 278 | 60 | 68 | 50 | 385 | 387 | 382 | -767 | -644 | -877 | 0 | 17 | 85 | 5083 | 5215 | 4993 | 1250
1129 | New RES at Minho region | TOOT | 43 | 44 | 42 | 13 | 19 | 8 | 50 | 52 | 50 | -170 | -105 | -243 | 0 | 4 | 19 | 651 | 654 | 648 | 400

## 2030NT-ENTSO-E
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_market_SEW |  |  | ΔRES
|  |  | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | low | mid | high | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year
1 | RES in north of Portugal | TOOT | 39 | 41 | 35 | 11 | 13 | 9 | 29 | 38 | 17 | -156 | -127 | -188 | 0 | 5 | 19 | 508 | 661 | 303
4 | Interconnection Portugal-Spain | TOOT | 10 | 17 | 3 | 4 | 7 | 0 | 6 | 9 | 2 | -55 | -2 | -106 | 0 | 2 | 7 | 115 | 168 | 33
16 | Biscay Gulf | TOOT | 239 | 259 | 209 | 96 | 106 | 88 | 115 | 127 | 105 | -1370 | -1262 | -1519 | 0 | 41 | 163 | 2051 | 2242 | 1813
26 | Reschenpass Interconnector Project | TOOT | 13 | 18 | 5 | 14 | 17 | 9 | 2 | 3 | 1 | -199 | -124 | -248 | 0 | 6 | 24 | 32 | 59 | 21
28 | Italy-Montenegro | PINT | 21 | 28 | 15 | 11 | 15 | 7 | 7 | 9 | 6 | -154 | -99 | -210 | 0 | 5 | 18 | 133 | 167 | 98
29 | Italy-Tunisia | TOOT | 16 | 30 | 3 | -83 | -82 | -84 | 9 | 11 | 8 | 1184 | 1194 | 1174 | 0 | 0 | 0 | 166 | 199 | 132
33 | Central Northern Italy | TOOT | 3 | 5 | 1 | 4 | 5 | 2 | 2 | 3 | 2 | -55 | -35 | -75 | 0 | 2 | 7 | 40 | 48 | 31
35 | CZ Southwest-east corridor | PINT | 46 | 50 | 41 | 28 | 31 | 25 | 13 | 20 | 10 | -403 | -355 | -444 | 0 | 12 | 48 | 241 | 370 | 169
40 | Belgium-Luxembourg-Germany: long-term perspective | light PINT | 12 | 13 | 11 | 7 | 8 | 6 | 4 | 7 | 2 | -99 | -88 | -107 | 0 | 3 | 12 | 77 | 130 | 35
47 | Westtirol (AT) - Vöhringen (DE) | PINT | 43 | 48 | 38 | 17 | 17 | 16 | 13 | 21 | 10 | -239 | -224 | -249 | 0 | 7 | 28 | 235 | 392 | 174
81 | North South Interconnector | TOOT | 87 | 92 | 82 | 32 | 35 | 25 | 29 | 39 | 17 | -450 | -353 | -504 | 0 | 14 | 54 | 514 | 688 | 312
85 | Integration of RES in Alentejo | TOOT | 26 | 36 | 16 | 4 | 7 | 2 | 34 | 43 | 28 | -57 | -27 | -94 | 0 | 2 | 7 | 607 | 759 | 526
94 | GerPol Improvements | TOOT | 101 | 102 | 100 | 122 | 126 | 115 | 16 | 20 | 11 | -1738 | -1644 | -1806 | 0 | 52 | 207 | 297 | 364 | 189
103 | Reinforcements Ring NL phase I | TOOT | 8 | 11 | 3 | 5 | 6 | 5 | 3 | 4 | 1 | -76 | -70 | -86 | 0 | 2 | 9 | 46 | 62 | 18
107 | Celtic Interconnector | TOOT | 145 | 162 | 122 | 36 | 38 | 32 | 94 | 102 | 84 | -508 | -454 | -542 | 0 | 15 | 60 | 1671 | 1802 | 1561
111 | Aurora line (3rd AC Finland-Sweden north) | TOOT | 45 | 48 | 42 | 16 | 17 | 15 | 4 | 4 | 4 | -230 | -220 | -240 | 0 | 7 | 27 | 69 | 69 | 69
120 | Belgian Modular Offshore Grid II (MOG II) | TOOT | 664 | 664 | 664 | 156 | 156 | 156 | 797 | 797 | 797 | -2226 | -2226 | -2226 | 0 | 67 | 265 | 13671 | 13671 | 13671
121 | Nautilus: multi-purpose interconnector Belgium - UK | PINT | 51 | 57 | 43 | 35 | 41 | 31 | 6 | 10 | 0 | -503 | -441 | -580 | 0 | 15 | 60 | 107 | 174 | 0
123 | LitPol Link Stage 2 | TOOT | 171 | 174 | 167 | 160 | 160 | 160 | 16 | 17 | 15 | -2290 | -2289 | -2291 | 0 | 69 | 273 | 278 | 293 | 264
124 | NordBalt phase 2 | PINT | 26 | 29 | 21 | 22 | 24 | 19 | 5 | 7 | 3 | -311 | -269 | -342 | 0 | 9 | 37 | 82 | 122 | 59
126 | SE North-south short-term reinforcements | TOOT | 39 | 49 | 24 | 22 | 30 | 16 | 5 | 5 | 4 | -318 | -228 | -427 | 0 | 10 | 38 | 82 | 86 | 78
127 | Central Southern Italy | TOOT | 7 | 10 | 3 | 0 | 2 | -2 | 3 | 3 | 1 | -1 | 32 | -35 | 0 | 0 | 0 | 45 | 57 | 27
130 | HVDC SuedOstLink Wolmirstedt to area Isar | TOOT | 245 | 245 | 245 | 12 | 12 | 12 | 69 | 69 | 69 | -421 | -421 | -421 | 0 | 13 | 50 | 686 | 686 | 686
132 | HVDC Line A-North | TOOT | 901 | 901 | 901 | 42 | 42 | 42 | 285 | 285 | 285 | -1503 | -1503 | -1503 | 0 | 45 | 179 | 2846 | 2846 | 2846
138 | Black Sea Corridor | TOOT | 6 | 7 | 4 | 3 | 9 | 0 | 1 | 1 | 0 | -47 | -3 | -124 | 0 | 1 | 6 | 9 | 18 | 4
142 | CSE4 | TOOT | 2 | 3 | 1 | 2 | 4 | 1 | 0 | 1 | 0 | -30 | -17 | -54 | 0 | 1 | 4 | 3 | 12 | -3
144 | Mid Continental East corridor | TOOT | 13 | 16 | 8 | 9 | 12 | 8 | 1 | 2 | 0 | -134 | -113 | -172 | 0 | 4 | 16 | 18 | 35 | 8
150 | Italy-Slovenia | light PINT | 14 | 19 | 11 | 13 | 18 | 11 | 2 | 4 | 0 | -190 | -155 | -256 | 0 | 6 | 23 | 40 | 65 | 0
153 | France-Alderney-Britain | PINT | 52 | 60 | 46 | 18 | 19 | 17 | 20 | 24 | 16 | -263 | -241 | -276 | 0 | 8 | 31 | 364 | 430 | 281
170 | Baltic States Synchronization with Continental Europe | TOOT | 231 | 252 | 200 | 221 | 230 | 207 | 32 | 48 | 20 | -3152 | -2961 | -3290 | 0 | 95 | 375 | 579 | 889 | 358
174 | Greenconnector | PINT | 34 | 39 | 28 | 40 | 42 | 39 | 2 | 4 | 0 | -578 | -560 | -596 | 0 | 17 | 69 | 30 | 75 | 5
176 | Hansa PowerBridge I | TOOT | 154 | 156 | 152 | 75 | 75 | 74 | 9 | 10 | 9 | -1065 | -1061 | -1068 | 0 | 32 | 127 | 162 | 173 | 152
183 | DKW-DE, Westcoast | TOOT | 53 | 60 | 41 | 31 | 37 | 22 | 5 | 13 | 2 | -447 | -320 | -535 | 0 | 13 | 53 | 87 | 231 | 31
186 | East of Austria | TOOT | 292 | 297 | 287 | 87 | 93 | 83 | 273 | 274 | 271 | -1215 | -1187 | -1266 | 0 | 37 | 147 | 4984 | 5108 | 4835
187 | St. Peter (AT) - Pleinting (DE) | PINT | 92 | 99 | 88 | 34 | 41 | 27 | 27 | 28 | 24 | -488 | -379 | -582 | 0 | 15 | 58 | 465 | 494 | 416
190 | NorthConnect | TOOT | 130 | 135 | 124 | 54 | 66 | 42 | 10 | 13 | 8 | -774 | -604 | -939 | 0 | 23 | 92 | 160 | 218 | 84
200 | CZ Northwest-South corridor | TOOT | 49 | 56 | 42 | 33 | 35 | 30 | 14 | 18 | 11 | -475 | -425 | -503 | 0 | 14 | 57 | 258 | 333 | 182
210 | Würmlach (AT) - Somplago (IT) interconnection | TOOT | 7 | 9 | 4 | 7 | 9 | 5 | 2 | 6 | 0 | -106 | -68 | -133 | 0 | 3 | 13 | 29 | 100 | 1
219 | EuroAsia Interconnector | TOOT | 80 | 85 | 76 | -41 | -8 | -74 | 1 | 1 | 0 | 582 | 1052 | 112 | 0 | 0 | 0 | 9 | 11 | 6
225 | 2nd interconnector Belgium - Germany | light PINT | 27 | 35 | 22 | 11 | 12 | 9 | 11 | 13 | 8 | -152 | -128 | -168 | 0 | 5 | 18 | 197 | 241 | 142
227 | Transbalkan Corridor | TOOT | 0 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | -12 | -3 | -32 | 0 | 0 | 1 | 3 | 11 | 0
228 | Muhlbach - Eichstetten | TOOT | 19 | 25 | 10 | 11 | 13 | 9 | 8 | 10 | 6 | -155 | -133 | -180 | 0 | 5 | 18 | 139 | 180 | 98
230 | GerPol Power Bridge I | TOOT | 311 | 321 | 304 | 416 | 429 | 402 | 29 | 30 | 28 | -5937 | -5749 | -6124 | 0 | 178 | 707 | 497 | 518 | 475
231 | Beznau - Tiengen | PINT | 41 | 44 | 38 | 13 | 17 | 11 | 18 | 25 | 12 | -193 | -155 | -237 | 0 | 6 | 23 | 323 | 460 | 197
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Bergrheinfeld West | TOOT | 2032 | 2032 | 2032 | 88 | 88 | 88 | 652 | 652 | 652 | -3160 | -3160 | -3160 | 0 | 95 | 376 | 6516 | 6516 | 6516
239 | Fenno-Skan 1 renewal | light PINT | 11 | 12 | 10 | 4 | 7 | 3 | 4 | 9 | 0 | -63 | -42 | -101 | 0 | 2 | 8 | 68 | 167 | 5
243 | New 400 kV interconnection line between Serbia and Croatia | light PINT | 10 | 18 | 5 | 7 | 16 | 0 | 2 | 2 | 1 | -105 | -5 | -224 | 0 | 3 | 12 | 28 | 39 | 9
244 | Vigy - Uchtelfangen area | PINT | 97 | 100 | 93 | 49 | 55 | 46 | 41 | 55 | 29 | -704 | -652 | -793 | 0 | 21 | 84 | 736 | 1018 | 493
247 | AQUIND Interconnector | PINT | 73 | 82 | 66 | 30 | 39 | 25 | 27 | 35 | 22 | -429 | -359 | -560 | 0 | 13 | 51 | 488 | 618 | 384
250 | Merchant line Castasegna (CH) - Mese (IT) | PINT | 8 | 13 | 3 | 6 | 10 | 0 | 1 | 3 | 0 | -89 | -6 | -139 | 0 | 3 | 11 | 17 | 47 | 0
252 | Internal Belgian Backbone Center-East: HTLS upgrade Massenhoven-VanEyck-Gramme-Courcelles-Bruegel-Mercator | PINT | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0
253 | Upstream reinforcement in France to increase FR-CH capacity | PINT | 14 | 15 | 13 | 10 | 16 | 7 | 2 | 3 | 0 | -149 | -95 | -223 | 0 | 4 | 18 | 32 | 47 | 5
254 | HVDC Ultranet Osterath to Philippsburg | TOOT | 90 | 90 | 90 | 5 | 5 | 5 | 27 | 27 | 27 | -196 | -196 | -196 | 0 | 6 | 23 | 275 | 275 | 275
259 | HU-RO | PINT | 11 | 12 | 10 | 4 | 5 | 3 | 1 | 2 | 0 | -58 | -44 | -75 | 0 | 2 | 7 | 16 | 43 | 4
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | PINT | 62 | 67 | 54 | 28 | 29 | 28 | 5 | 10 | 0 | -407 | -405 | -407 | 0 | 12 | 48 | -816 | 180 | -1811
263 | Lake Constance East | light PINT | 85 | 92 | 79 | 36 | 44 | 28 | 25 | 25 | 24 | -513 | -407 | -621 | 0 | 15 | 61 | 433 | 449 | 416
267 | Hansa PowerBridge II | light PINT | 144 | 147 | 141 | 65 | 65 | 65 | 6 | 6 | 6 | -926 | -924 | -927 | 0 | 28 | 110 | 106 | 107 | 105
270 | FR-ES project -Aragón-Atlantic Pyrenees | PINT | 125 | 132 | 116 | 43 | 49 | 37 | 60 | 63 | 56 | -616 | -532 | -703 | 0 | 18 | 73 | 1075 | 1166 | 974
276 | FR-ES project -Navarra-Landes | PINT | 125 | 132 | 116 | 43 | 49 | 37 | 60 | 63 | 56 | -616 | -532 | -703 | 0 | 18 | 73 | 1075 | 1166 | 974
280 | FR-BE: study Lonny-Achene-Gramme | PINT | 44 | 46 | 41 | 25 | 30 | 20 | 15 | 20 | 12 | -364 | -287 | -424 | 0 | 11 | 43 | 271 | 374 | 202
283 | TuNur Italy | PINT | 3 | 6 | 0 | 259 | 271 | 247 | 702 | 732 | 673 | -3706 | -3535 | -3877 | 0 | 111 | 441 | 12646 | 12877 | 12415
285 | GridLink | PINT | 52 | 60 | 46 | 18 | 19 | 17 | 20 | 24 | 16 | -263 | -241 | -276 | 0 | 8 | 31 | 364 | 430 | 281
286 | Greenlink | PINT | 33 | 39 | 30 | 19 | 20 | 18 | 28 | 36 | 24 | -267 | -251 | -282 | 0 | 8 | 32 | 504 | 662 | 410
293 | Southern Aegean Interconnector | PINT | 82 | 88 | 72 | 29 | 30 | 26 | 76 | 80 | 75 | -412 | -372 | -433 | 0 | 12 | 49 | 1356 | 1384 | 1321
297 | BRABO II + III | TOOT | 18 | 21 | 15 | 4 | 5 | 2 | 17 | 21 | 11 | -50 | -24 | -67 | 0 | 2 | 6 | 306 | 372 | 194
299 | SACOI3 | TOOT | 110 | 118 | 103 | 32 | 35 | 30 | 4 | 6 | 2 | -451 | -425 | -500 | 0 | 14 | 54 | 68 | 114 | 39
309 | NeuConnect | TOOT | 56 | 67 | 41 | 63 | 67 | 60 | 11 | 19 | 0 | -904 | -861 | -957 | 0 | 27 | 108 | 188 | 337 | 0
312 | St. Peter (AT) - Tauern (AT) | TOOT | 162 | 169 | 152 | 57 | 64 | 53 | 58 | 68 | 45 | -1036 | -777 | -1284 | 0 | 25 | 97 | 1035 | 1264 | 792
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | TOOT | 166 | 172 | 159 | 72 | 81 | 64 | 54 | 68 | 40 | -1035 | -921 | -1160 | 0 | 31 | 123 | 963 | 1264 | 685
323 | Dekani (SI) - Zaule (IT) interconnection | TOOT | 1 | 2 | 1 | 0 | 1 | -2 | 1 | 1 | 0 | 5 | 32 | -19 | 0 | 0 | 0 | 11 | 24 | 1
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | TOOT | 7 | 16 | 1 | 1 | 1 | 1 | 1 | 2 | 0 | -12 | -10 | -15 | 0 | 0 | 1 | 18 | 44 | 0
325 | Obersielach (AT) - Podlog (SI) | PINT | 20 | 26 | 14 | 22 | 27 | 17 | 3 | 5 | 2 | -309 | -248 | -383 | 0 | 9 | 37 | 50 | 96 | 29
328 | Interconnector DE-LUX | TOOT | 0 | 1 | 0 | 0 | 0 | -1 | 0 | 1 | 0 | 5 | 21 | -6 | 0 | 0 | 0 | 4 | 11 | 0
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | TOOT | 416 | 416 | 416 | 149 | 149 | 149 | 324 | 324 | 324 | -2134 | -2134 | -2134 | 0 | 64 | 254 | 5561 | 5561 | 5561
330 | 4th 400kV CZ-SK interconnector | light PINT | 5 | 11 | 1 | 3 | 5 | 1 | 0 | 1 | 0 | -50 | -12 | -78 | 0 | 1 | 6 | 9 | 27 | 0
333 | PST Foretaille | PINT | 81 | 86 | 75 | 46 | 52 | 43 | 1 | 2 | 0 | -658 | -611 | -741 | 0 | 20 | 78 | 18 | 42 | 0
335 | North Sea Wind Power Hub | light PINT | 871 | 908 | 825 | 699 | 714 | 683 | 3206 | 3309 | 3088 | -9984 | -9764 | -10204 | 0 | 300 | 1188 | 56486 | 56964 | 55767
338 | Adriatic HVDC link | PINT | 17 | 23 | 10 | 8 | 8 | 8 | 7 | 12 | 2 | -113 | -110 | -116 | 0 | 3 | 13 | 124 | 213 | 35
339 | Tyrrhenian link | PINT | 3 | 6 | 0 | 3 | 4 | 2 | 3 | 4 | 1 | -49 | -35 | -64 | 0 | 1 | 6 | 49 | 75 | 24
340 | Avelgem-Courcelles (Boucle du Hainaut): new corridor | TOOT | 203 | 203 | 203 | 73 | 73 | 73 | 146 | 146 | 146 | -1041 | -1041 | -1041 | 0 | 31 | 124 | 2509 | 2509 | 2509
341 | North CSE Corridor | PINT | 1 | 2 | 1 | 1 | 2 | -1 | 0 | 1 | 0 | -16 | 11 | -32 | 0 | 0 | 2 | 6 | 12 | 0
342 | Central Balkan Corridor | PINT | 3 | 7 | 0 | 3 | 11 | -1 | 0 | 1 | 0 | -48 | 11 | -161 | 0 | 1 | 6 | 8 | 22 | 0
343 | CSE1 New | PINT | 3 | 4 | 3 | 2 | 3 | 0 | 0 | 1 | 0 | -26 | 1 | -40 | 0 | 1 | 3 | 9 | 15 | 0
346 | ZuidWest380 NL Oost | PINT | 14 | 17 | 10 | 2 | 2 | 2 | 10 | 13 | 5 | -27 | -23 | -33 | 0 | 1 | 3 | 180 | 232 | 82
349 | MaresConnect | PINT | 48 | 50 | 46 | 26 | 28 | 24 | 43 | 51 | 36 | -374 | -344 | -407 | 0 | 11 | 45 | 765 | 934 | 644
350 | South Balkan Corridor | TOOT | 3 | 8 | 1 | 0 | 4 | -2 | 0 | 0 | 0 | 3 | 34 | -64 | 0 | 0 | 0 | 3 | 9 | -2
375 | Lienz (AT) - Veneto region (IT) 220 kV | PINT | 16 | 17 | 14 | 18 | 23 | 14 | 2 | 4 | 1 | -255 | -196 | -328 | 0 | 8 | 30 | 44 | 83 | 12
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | light PINT | 2 | 5 | 0 | 2 | 7 | -1 | 0 | 1 | 0 | -31 | 20 | -93 | 0 | 1 | 4 | 6 | 16 | 0
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | PINT | 14 | 17 | 10 | 2 | 3 | 2 | 10 | 13 | 5 | -28 | -23 | -36 | 0 | 1 | 3 | 180 | 232 | 82
378 | Transformer Gatica | TOOT | [12 empty] | 0 | 0 | 0
379 | Uprate Gatica lines | TOOT | [12 empty] | 0 | 0 | 0
1034 | HVDC corridor from Northern Germany to Western Germany | PINT | 876 | 876 | 876 | 34 | 34 | 34 | 267 | 267 | 267 | -1209 | -1209 | -1209 | 0 | 36 | 144 | 2665 | 2665 | 2665
1039 | SE North-south long-term reinforcements | light PINT | 9 | 11 | 6 | 7 | 12 | 2 | 4 | 10 | 1 | -97 | -31 | -169 | 0 | 3 | 12 | 75 | 185 | 15
1040 | LirIC | PINT | 53 | 53 | 53 | 20 | 21 | 19 | 29 | 37 | 24 | -281 | -268 | -299 | 0 | 8 | 33 | 524 | 688 | 428
1041 | GREGY Green Energy Interconnector | PINT | 46 | 48 | 44 | 45 | 99 | 7 | 1 | 3 | 0 | -642 | -95 | -1411 | 0 | 19 | 76 | 22 | 55 | 3
1042 | Offshore Wind LT 1 | PINT | 73 | 79 | 69 | 15 | 21 | 10 | 132 | 148 | 113 | -217 | -147 | -295 | 0 | 7 | 26 | 2322 | 2566 | 2078
1046 | Finnish North-South reinforcement | PINT | 10 | 10 | 10 | 0 | 0 | 0 | 10 | 10 | 10 | -4 | -4 | -4 | 0 | 0 | 1 | 186 | 186 | 186
1047 | Emden-Eemshaven | light PINT | 15 | 16 | 14 | 7 | 8 | 5 | 3 | 4 | 2 | -97 | -66 | -119 | 0 | 3 | 12 | 61 | 72 | 42
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | PINT | 26 | 29 | 20 | 83 | 88 | 79 | 1 | 2 | 0 | -1191 | -1126 | -1263 | 0 | 36 | 142 | 16 | 45 | 0
1049 | Cronos Energy Ltd | PINT | 58 | 59 | 58 | 42 | 45 | 39 | 3 | 9 | 0 | -594 | -558 | -643 | 0 | 18 | 71 | 54 | 163 | 0
1050 | Tarchon Energy Ltd | PINT | 51 | 57 | 43 | 56 | 61 | 53 | 11 | 19 | 0 | -797 | -757 | -870 | 0 | 24 | 95 | 187 | 339 | 0
1051 | Aminth Energy Ltd | PINT | 56 | 59 | 54 | 28 | 35 | 25 | 9 | 14 | 0 | -402 | -351 | -501 | 0 | 12 | 48 | 156 | 253 | 0
1052 | Lienz (AT) - Obersielach (AT) | PINT | 23 | 26 | 20 | 22 | 24 | 17 | 2 | 5 | 0 | -277 | -236 | -346 | 0 | 9 | 37 | 45 | 96 | 5
1054 | Westtirol (AT) - Zell/Ziller (AT) | PINT | 42 | 48 | 38 | 17 | 18 | 16 | 12 | 21 | 3 | -241 | -224 | -258 | 0 | 7 | 29 | 211 | 392 | 53
1055 | Interconnection of Crete to the Mainland System of Greece | TOOT | 86 | 109 | 66 | -101 | -80 | -125 | 0 | 1 | 0 | 1439 | 1789 | 1136 | 0 | 0 | 0 | 6 | 27 | -9
1058 | HVDC Interconnector DE-CH | light PINT | 73 | 75 | 70 | 30 | 34 | 23 | 23 | 23 | 23 | -432 | -335 | -484 | 0 | 13 | 51 | 405 | 406 | 404
1059 | Southern Italy | PINT | 3 | 5 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | -1 | 2 | -4 | 0 | 0 | 0 | 10 | 17 | 3
1066 | Bulgaria - Turkey | light PINT | 81 | 86 | 75 | -216 | -205 | -228 | 1 | 2 | 0 | 3085 | 3259 | 2926 | 0 | 0 | 0 | 17 | 31 | 4
1067 | New AC 400 kV interconnection line Greece - Turkey | light PINT | 46 | 56 | 40 | -116 | -113 | -119 | 1 | 1 | 0 | 1652 | 1702 | 1613 | 0 | 0 | 0 | 9 | 19 | -2
1068 | LaSGo Link | light PINT | 30 | 33 | 23 | 24 | 26 | 21 | 4 | 8 | 2 | -337 | -301 | -378 | 0 | 10 | 40 | 77 | 145 | 43
1074 | Pannonian Corridor | PINT | 11 | 20 | 6 | 5 | 8 | 2 | 1 | 2 | 1 | -76 | -32 | -116 | 0 | 2 | 9 | 20 | 33 | 14
1082 | Sea-Socket | light PINT | 103 | 111 | 96 | 25 | 26 | 24 | 120 | 124 | 116 | -360 | -346 | -377 | 0 | 11 | 43 | 2135 | 2219 | 2047
1085 | Malta-Italy Cable Link No.2 | PINT | 0 | 0 | 0 | -22 | -20 | -24 | 1 | 3 | 0 | 318 | 341 | 282 | 0 | 0 | 0 | 19 | 50 | 4
1086 | Estonia internal grid reinforcement to increase RES connection capability (RRF project) | PINT | 65 | 67 | 63 | 13 | 15 | 11 | 124 | 124 | 123 | -182 | -152 | -211 | 0 | 5 | 22 | 2135 | 2139 | 2131
1088 | Latvia and Estonia Hybrid Off-Shore interconnector | PINT | 24 | 31 | 15 | 23 | 29 | 16 | 207 | 219 | 186 | -328 | -222 | -419 | 0 | 10 | 39 | 3599 | 3793 | 3284
1092 | Triton Link: offshore hybrid HVDC interconnector Belgium – Denmark | PINT | 160 | 173 | 147 | 166 | 169 | 160 | 745 | 787 | 693 | -2371 | -2281 | -2421 | 0 | 71 | 282 | 13126 | 13485 | 12791
1094 | Estlink 3 | light PINT | 25 | 25 | 24 | 28 | 32 | 23 | 1 | 3 | 0 | -400 | -329 | -457 | 0 | 12 | 48 | 26 | 62 | 3
1095 | Aurora line 2 (4th AC Finland-Sweden north) | light PINT | 21 | 24 | 19 | 7 | 8 | 7 | 1 | 1 | 0 | -104 | -98 | -109 | 0 | 3 | 12 | 13 | 23 | 3
1096 | Beznau - Mettlen | PINT | 48 | 51 | 43 | 17 | 23 | 13 | 14 | 16 | 14 | -244 | -183 | -322 | 0 | 7 | 29 | 320 | 519 | 232
1097 | Upgrade to Konti-Skan | PINT | 98 | 126 | 74 | 33 | 34 | 32 | 11 | 13 | 8 | -471 | -458 | -485 | 0 | 14 | 56 | 202 | 238 | 153
1098 | Offshore Wind LT 2 | PINT | 74 | 80 | 70 | 16 | 21 | 10 | 129 | 148 | 113 | -227 | -147 | -295 | 0 | 7 | 27 | 2291 | 2566 | 2081
1100 | Reinforcement of the existing CZ-DE interconnector (Hradec - Röhrsdorf) on the CZ side | PINT | 49 | 55 | 44 | 31 | 33 | 28 | 15 | 20 | 9 | -440 | -405 | -473 | 0 | 13 | 52 | 273 | 364 | 154
1102 | Mettlen - Ulrichen | light PINT | 15 | 19 | 13 | 4 | 5 | 3 | 6 | 9 | 4 | -64 | -43 | -77 | 0 | 2 | 8 | 100 | 160 | 64
1103 | Bickigen - Chippis | PINT | 37 | 45 | 30 | 12 | 13 | 11 | 13 | 20 | 10 | -172 | -164 | -180 | 0 | 5 | 20 | 242 | 365 | 163
1104 | Niederstedem - Roost | PINT | 0 | 0 | 0 | -1 | 0 | -1 | 0 | 1 | 0 | 9 | 19 | 0 | 0 | 0 | 0 | 6 | 17 | 0
1105 | Georgia-Romania Black Sea (submarine) interconnection cable project | PINT | 13 | 15 | 9 | -47 | -33 | -66 | 0 | 1 | 0 | 667 | 946 | 470 | 0 | 0 | 0 | 8 | 11 | 3
1106 | Bornholm Energy Island (BEI) | TOOT | 62 | 70 | 51 | 99 | 103 | 94 | 404 | 419 | 387 | -1420 | -1347 | -1467 | 0 | 43 | 169 | 7013 | 7182 | 6808
1107 | EuroAfrica Interconnector | PINT | 3 | 8 | 0 | 39 | 49 | 28 | 1 | 2 | 0 | -551 | -394 | -703 | 0 | 17 | 66 | 15 | 39 | 0
1109 | Basilicata - Campania reinforcements | PINT | 4 | 8 | 0 | 0 | 0 | 0 | 1 | 2 | 1 | -5 | -5 | -6 | 0 | 0 | 1 | 24 | 38 | 10
1110 | Sicily - Calabria | PINT | 2 | 5 | 0 | -1 | 0 | -2 | 1 | 2 | 1 | 15 | 23 | 6 | 0 | 0 | 0 | 25 | 35 | 15
1112 | GRITA 2 | PINT | 19 | 28 | 14 | 6 | 6 | 5 | 5 | 8 | 3 | -85 | -77 | -93 | 0 | 3 | 10 | 93 | 156 | 51
1119 | Bisamberg (AT) - Wien SO (AT) - Parndorf (AT) | PINT | 330 | 330 | 330 | 107 | 107 | 107 | 341 | 341 | 341 | -1471 | -1471 | -1471 | 0 | 46 | 183 | 6003 | 6003 | 6003
1120 | Wien SO (AT) – Ternitz (AT) – Hessenberg (AT) | PINT | 74 | 74 | 74 | 35 | 35 | 35 | 76 | 76 | 76 | -378 | -378 | -378 | 0 | 15 | 60 | 1338 | 1338 | 1338
1121 | Hessenberg (AT) - Weißenbach (AT) | PINT | 47 | 47 | 47 | 20 | 20 | 20 | 51 | 51 | 51 | -266 | -266 | -266 | 0 | 9 | 34 | 902 | 902 | 902
1122 | Offshore Wind connection Centre Manche 1 | TOOT | 190 | 196 | 183 | 35 | 36 | 33 | 253 | 256 | 251 | -499 | -470 | -521 | 0 | 15 | 59 | 4392 | 4453 | 4290
1123 | Offshore Wind Connection Centre Manche 2 | PINT | 224 | 228 | 220 | 40 | 45 | 35 | 294 | 306 | 275 | -578 | -496 | -642 | 0 | 17 | 69 | 5234 | 5312 | 5086
1124 | Offshore Wind Connection South Britanny | TOOT | 47 | 49 | 42 | 9 | 11 | 7 | 59 | 62 | 55 | -122 | -95 | -162 | 0 | 4 | 15 | 1059 | 1090 | 1017
1125 | Offshore Wind Connection Occitanie | TOOT | 51 | 52 | 51 | 9 | 10 | 7 | 59 | 61 | 56 | -125 | -95 | -150 | 0 | 4 | 15 | 1050 | 1063 | 1040
1126 | Offshore Wind Connection PACA | TOOT | 47 | 50 | 44 | 9 | 10 | 9 | 58 | 60 | 56 | -135 | -124 | -147 | 0 | 4 | 16 | 1038 | 1044 | 1030
1127 | Offshore Wind Connection South Atlantic | PINT | 196 | 202 | 189 | 39 | 41 | 35 | 267 | 276 | 259 | -550 | -506 | -587 | 0 | 17 | 65 | 4598 | 4607 | 4590
1129 | New RES at Minho region | TOOT | 43 | 47 | 38 | 9 | 11 | 8 | 49 | 52 | 45 | -130 | -112 | -164 | 0 | 4 | 15 | 867 | 901 | 826

## 2030DE-ENTSO-E
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_market_SEW |  |  | ΔRES
|  |  | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | low | mid | high | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year
1 | RES in north of Portugal | TOOT | 60 | 66 | 56 | 24 | 27 | 18 | 59 | 76 | 41 | -307 | -233 | -345 | 0 | 7 | 34 | 890 | 1036 | 737
4 | Interconnection Portugal-Spain | TOOT | 17 | 27 | 8 | 6 | 9 | 3 | 18 | 27 | 13 | -71 | -39 | -116 | 0 | 2 | 8 | 304 | 469 | 204
16 | Biscay Gulf | TOOT | 325 | 336 | 312 | 109 | 118 | 95 | 292 | 294 | 289 | -1392 | -1222 | -1518 | 0 | 31 | 154 | 5525 | 6148 | 5107
26 | Reschenpass Interconnector Project | TOOT | 18 | 25 | 9 | 16 | 17 | 14 | 3 | 6 | 2 | -202 | -185 | -219 | 0 | 4 | 22 | 58 | 91 | 32
28 | Italy-Montenegro | PINT | 25 | 29 | 21 | 13 | 14 | 12 | 26 | 28 | 23 | -163 | -152 | -173 | 0 | 4 | 18 | 426 | 500 | 352
29 | Italy-Tunisia | TOOT | 52 | 62 | 43 | -61 | -58 | -64 | 59 | 64 | 53 | 782 | 818 | 746 | 0 | 0 | 0 | 955 | 976 | 934
33 | Central Northern Italy | TOOT | 18 | 20 | 15 | 13 | 15 | 11 | 20 | 23 | 17 | -166 | -140 | -192 | 0 | 4 | 18 | 328 | 353 | 304
35 | CZ Southwest-east corridor | PINT | 30 | 34 | 25 | 6 | 8 | 3 | 10 | 13 | 7 | -74 | -33 | -108 | 0 | 2 | 8 | 163 | 233 | 119
40 | Belgium-Luxembourg-Germany: long-term perspective | light PINT | 26 | 36 | 15 | 15 | 18 | 10 | 5 | 6 | 4 | -186 | -122 | -231 | 0 | 4 | 21 | 86 | 94 | 71
47 | Westtirol (AT) - Vöhringen (DE) | PINT | 47 | 51 | 40 | 22 | 27 | 19 | 5 | 10 | 2 | -279 | -246 | -341 | 0 | 6 | 31 | 88 | 176 | 41
81 | North South Interconnector | TOOT | 78 | 78 | 78 | 33 | 33 | 33 | 31 | 31 | 31 | -418 | -418 | -418 | 0 | 9 | 46 | 548 | 548 | 548
85 | Integration of RES in Alentejo | TOOT | 14 | 20 | 10 | 4 | 5 | 2 | 23 | 28 | 17 | -46 | -31 | -65 | 0 | 1 | 5 | 395 | 502 | 301
94 | GerPol Improvements | TOOT | 177 | 200 | 144 | 119 | 125 | 114 | 53 | 61 | 48 | -1521 | -1462 | -1600 | 0 | 33 | 169 | 902 | 930 | 852
103 | Reinforcements Ring NL phase I | TOOT | 28 | 31 | 27 | 13 | 16 | 7 | 10 | 10 | 10 | -165 | -95 | -205 | 0 | 4 | 18 | 168 | 176 | 153
107 | Celtic Interconnector | TOOT | 81 | 152 | 0 | 38 | 40 | 37 | 105 | 105 | 105 | -490 | -470 | -519 | 0 | 11 | 54 | 1883 | 1910 | 1853
111 | Aurora line (3rd AC Finland-Sweden north) | TOOT | 74 | 83 | 63 | 10 | 14 | 7 | 68 | 75 | 63 | -132 | -86 | -181 | 0 | 3 | 15 | 1144 | 1287 | 962
120 | Belgian Modular Offshore Grid II (MOG II) | TOOT | 734 | 737 | 729 | 197 | 201 | 192 | 833 | 856 | 810 | -2527 | -2459 | -2573 | 0 | 56 | 280 | 14673 | 14752 | 14572
121 | Nautilus: multi-purpose interconnector Belgium - UK | PINT | 1 | 1 | 1 | -45 | -45 | -45 | 2 | 2 | 2 | 576 | 576 | 576 | 10 | 0 | 0 | 45 | 45 | 45
123 | LitPol Link Stage 2 | TOOT | 194 | 196 | 193 | 160 | 164 | 154 | 51 | 64 | 40 | -2052 | -1971 | -2105 | 0 | 45 | 228 | 844 | 984 | 707
124 | NordBalt phase 2 | PINT | 45 | 47 | 43 | 10 | 11 | 10 | 27 | 28 | 26 | -130 | -124 | -142 | 0 | 3 | 14 | 449 | 471 | 428
126 | SE North-south short-term reinforcements | TOOT | 110 | 121 | 103 | 27 | 32 | 23 | 52 | 54 | 49 | -340 | -300 | -416 | 0 | 7 | 38 | 903 | 925 | 880
127 | Central Southern Italy | TOOT | 36 | 45 | 29 | 12 | 13 | 10 | 44 | 50 | 41 | -148 | -127 | -168 | 0 | 3 | 16 | 750 | 762 | 743
130 | HVDC SuedOstLink Wolmirstedt to area Isar | TOOT | 2008 | 2008 | 2008 | 52 | 52 | 52 | 343 | 343 | 343 | -1858 | -1858 | -1858 | 0 | 41 | 206 | 3426 | 3426 | 3426
132 | HVDC Line A-North | TOOT | 5283 | 5283 | 5283 | 129 | 129 | 129 | 896 | 896 | 896 | -4605 | -4605 | -4605 | 0 | 101 | 511 | 8961 | 8961 | 8961
138 | Black Sea Corridor | TOOT | 41 | 42 | 40 | 22 | 25 | 19 | 19 | 25 | 15 | -279 | -243 | -325 | 0 | 6 | 31 | 319 | 374 | 269
142 | CSE4 | TOOT | 11 | 14 | 8 | 5 | 8 | 2 | 10 | 16 | 4 | -58 | -24 | -108 | 0 | 1 | 6 | 161 | 237 | 77
144 | Mid Continental East corridor | TOOT | 106 | 116 | 95 | 63 | 67 | 58 | 57 | 68 | 48 | -811 | -748 | -853 | 0 | 18 | 90 | 955 | 1035 | 845
150 | Italy-Slovenia | light PINT | 48 | 53 | 45 | 33 | 36 | 29 | 10 | 15 | 5 | -418 | -369 | -465 | 0 | 9 | 46 | 174 | 266 | 75
153 | France-Alderney-Britain | PINT | 48 | 48 | 48 | -27 | -27 | -27 | 28 | 28 | 28 | 345 | 345 | 345 | 6 | 0 | 0 | 484 | 484 | 484
170 | Baltic States Synchronization with Continental Europe | TOOT | 263 | 283 | 242 | 227 | 236 | 215 | 76 | 100 | 58 | -2915 | -2761 | -3024 | 0 | 64 | 324 | 1276 | 1525 | 1027
174 | Greenconnector | PINT | 51 | 51 | 50 | 35 | 39 | 28 | 6 | 7 | 5 | -451 | -365 | -497 | 0 | 10 | 50 | 104 | 120 | 75
176 | Hansa PowerBridge I | TOOT | 242 | 245 | 238 | 110 | 112 | 108 | 60 | 68 | 51 | -1410 | -1385 | -1434 | 0 | 31 | 156 | 1043 | 1174 | 911
183 | DKW-DE, Westcoast | TOOT | 213 | 229 | 195 | 88 | 96 | 80 | 118 | 126 | 106 | -1127 | -1026 | -1228 | 0 | 25 | 125 | 2145 | 2325 | 1872
186 | East of Austria | TOOT | 300 | 310 | 289 | 94 | 97 | 93 | 324 | 324 | 323 | -1210 | -1190 | -1245 | 0 | 27 | 134 | 5807 | 5858 | 5714
187 | St. Peter (AT) - Pleinting (DE) | PINT | 108 | 128 | 81 | 49 | 52 | 47 | 11 | 14 | 8 | -631 | -597 | -664 | 0 | 14 | 70 | 192 | 217 | 129
190 | NorthConnect | TOOT | 232 | 232 | 232 | 62 | 62 | 62 | 38 | 38 | 38 | -790 | -790 | -790 | 0 | 17 | 88 | 676 | 676 | 676
200 | CZ Northwest-South corridor | TOOT | 54 | 60 | 48 | 11 | 14 | 10 | 9 | 14 | 7 | -145 | -123 | -186 | 0 | 3 | 16 | 153 | 210 | 121
210 | Würmlach (AT) - Somplago (IT) interconnection | TOOT | 9 | 14 | 1 | 9 | 10 | 9 | 3 | 7 | 0 | -121 | -114 | -131 | 0 | 3 | 13 | 52 | 134 | 6
219 | EuroAsia Interconnector | TOOT | 528 | 642 | 414 | 12 | 28 | -5 | 320 | 349 | 291 | -149 | 58 | -356 | 0 | 3 | 17 | 5227 | 5314 | 5141
225 | 2nd interconnector Belgium - Germany | light PINT | 40 | 55 | 23 | 25 | 32 | 16 | 12 | 14 | 10 | -326 | -205 | -405 | 0 | 7 | 36 | 211 | 251 | 170
227 | Transbalkan Corridor | TOOT | 20 | 24 | 14 | 13 | 16 | 11 | 14 | 16 | 13 | -168 | -136 | -204 | 0 | 4 | 19 | 299 | 459 | 227
228 | Muhlbach - Eichstetten | TOOT | 42 | 47 | 34 | 21 | 21 | 20 | 5 | 6 | 4 | -266 | -259 | -272 | 0 | 6 | 29 | 88 | 97 | 71
230 | GerPol Power Bridge I | TOOT | 374 | 379 | 368 | 335 | 337 | 333 | 22 | 26 | 17 | -4297 | -4272 | -4323 | 0 | 95 | 477 | 376 | 453 | 300
231 | Beznau - Tiengen | PINT | 30 | 33 | 28 | 13 | 19 | 8 | 7 | 8 | 5 | -171 | -100 | -240 | 0 | 4 | 19 | 119 | 138 | 93
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Bergrheinfeld West | TOOT | 9782 | 9782 | 9782 | 238 | 238 | 238 | 1689 | 1689 | 1689 | -8496 | -8496 | -8496 | 0 | 187 | 943 | 16890 | 16890 | 16890
239 | Fenno-Skan 1 renewal | light PINT | 29 | 38 | 22 | 4 | 7 | 2 | 35 | 39 | 28 | -49 | -24 | -86 | 0 | 1 | 5 | 581 | 655 | 489
243 | New 400 kV interconnection line between Serbia and Croatia | light PINT | 12 | 21 | 7 | 4 | 6 | 3 | 4 | 9 | 1 | -56 | -44 | -78 | 0 | 1 | 6 | 68 | 157 | 23
244 | Vigy - Uchtelfangen area | PINT | 172 | 209 | 134 | 96 | 103 | 88 | 25 | 28 | 20 | -1226 | -1135 | -1316 | 0 | 27 | 136 | 434 | 506 | 305
247 | AQUIND Interconnector | PINT | 59 | 59 | 59 | -38 | -38 | -38 | 29 | 29 | 29 | 482 | 482 | 482 | 9 | 0 | 0 | 514 | 514 | 514
250 | Merchant line Castasegna (CH) - Mese (IT) | PINT | 11 | 12 | 8 | 7 | 9 | 3 | 3 | 6 | 0 | -86 | -36 | -111 | 0 | 2 | 10 | 45 | 114 | 7
252 | Internal Belgian Backbone Center-East: HTLS upgrade Massenhoven-VanEyck-Gramme-Courcelles-Bruegel-Mercator | PINT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253 | Upstream reinforcement in France to increase FR-CH capacity | PINT | 38 | 47 | 34 | 11 | 14 | 9 | 4 | 8 | 2 | -141 | -118 | -182 | 0 | 3 | 16 | 67 | 133 | 26
254 | HVDC Ultranet Osterath to Philippsburg | TOOT | 447 | 447 | 447 | 12 | 12 | 12 | 47 | 47 | 47 | -411 | -411 | -411 | 0 | 14 | 50 | 465 | 465 | 465
259 | HU-RO | PINT | 43 | 49 | 39 | 23 | 25 | 19 | 25 | 30 | 22 | -290 | -240 | -324 | 0 | 6 | 32 | 429 | 474 | 375
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | PINT | 0 | 0 | 0 | -41 | -40 | -42 | 18 | 21 | 15 | 521 | 535 | 506 | 0 | 0 | 0 | 305 | 380 | 231
263 | Lake Constance East | light PINT | 120 | 124 | 116 | 58 | 60 | 56 | 12 | 15 | 10 | -750 | -716 | -767 | 0 | 16 | 83 | 205 | 261 | 173
267 | Hansa PowerBridge II | light PINT | 205 | 205 | 205 | 102 | 104 | 100 | 54 | 61 | 48 | -1306 | -1279 | -1332 | 0 | 29 | 145 | 948 | 1051 | 845
270 | FR-ES project -Aragón-Atlantic Pyrenees | PINT | 175 | 180 | 172 | 56 | 64 | 50 | 170 | 175 | 165 | -723 | -642 | -824 | 0 | 16 | 80 | 3045 | 3163 | 2977
276 | FR-ES project -Navarra-Landes | PINT | 175 | 180 | 172 | 56 | 64 | 50 | 170 | 175 | 165 | -723 | -642 | -824 | 0 | 16 | 80 | 3045 | 3163 | 2977
280 | FR-BE: study Lonny-Achene-Gramme | PINT | 101 | 106 | 95 | 43 | 49 | 39 | 4 | 7 | 2 | -546 | -498 | -631 | 0 | 12 | 61 | 69 | 123 | 37
283 | TuNur Italy | PINT | 16 | 16 | 16 | 195 | 203 | 187 | 0 | 0 | 0 | -2500 | -2400 | -2600 | 0 | 55 | 278 | 0 | 0 | 0
285 | GridLink | PINT | 48 | 48 | 48 | -27 | -27 | -27 | 28 | 28 | 28 | 345 | 345 | 345 | 6 | 0 | 0 | 484 | 484 | 484
286 | Greenlink | PINT | 15 | 15 | 15 | -1 | -1 | -1 | 74 | 74 | 74 | 13 | 13 | 13 | 0 | 0 | 0 | 1305 | 1305 | 1305
293 | Southern Aegean Interconnector | PINT | 60 | 63 | 58 | 21 | 24 | 19 | 65 | 68 | 63 | -274 | -244 | -307 | 0 | 6 | 30 | 1094 | 1134 | 1035
297 | BRABO II + III | TOOT | 29 | 44 | 8 | 17 | 19 | 15 | 22 | 28 | 19 | -222 | -191 | -248 | 0 | 5 | 25 | 373 | 430 | 336
299 | SACOI3 | TOOT | 78 | 89 | 64 | 32 | 37 | 27 | 57 | 65 | 49 | -414 | -346 | -472 | 0 | 9 | 46 | 965 | 1024 | 882
309 | NeuConnect | TOOT | 17 | 17 | 17 | -9 | -9 | -9 | 12 | 12 | 12 | 120 | 120 | 120 | 2 | 0 | 0 | 214 | 214 | 214
312 | St. Peter (AT) - Tauern (AT) | TOOT | 150 | 158 | 143 | 82 | 91 | 77 | 28 | 30 | 25 | -1052 | -993 | -1168 | 0 | 23 | 117 | 471 | 500 | 452
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | TOOT | 168 | 198 | 143 | 90 | 107 | 77 | 24 | 30 | 19 | -1148 | -993 | -1373 | 0 | 25 | 127 | 417 | 500 | 319
323 | Dekani (SI) - Zaule (IT) interconnection | TOOT | 2 | 4 | 0 | 1 | 3 | -1 | 1 | 2 | 1 | -7 | 19 | -43 | 0 | 0 | 1 | 25 | 28 | 21
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | TOOT | 3 | 5 | 1 | 3 | 5 | 1 | 2 | 3 | 2 | -36 | -10 | -68 | 0 | 1 | 4 | 39 | 48 | 25
325 | Obersielach (AT) - Podlog (SI) | PINT | 16 | 21 | 11 | 12 | 16 | 10 | 4 | 6 | 3 | -151 | -128 | -205 | 0 | 3 | 17 | 73 | 114 | 59
328 | Interconnector DE-LUX | TOOT | 2 | 5 | 1 | 2 | 2 | 1 | 1 | 2 | 1 | -19 | -13 | -28 | 0 | 0 | 2 | 23 | 43 | 11
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
330 | 4th 400kV CZ-SK interconnector | light PINT | 14 | 22 | 8 | 9 | 12 | 3 | 2 | 5 | 0 | -110 | -38 | -154 | 0 | 2 | 12 | 29 | 94 | 4
333 | PST Foretaille | PINT | 105 | 109 | 101 | 50 | 55 | 47 | 7 | 12 | 4 | -638 | -604 | -700 | 0 | 14 | 71 | 126 | 220 | 53
335 | North Sea Wind Power Hub | light PINT | 924 | 941 | 901 | 846 | 859 | 836 | 3142 | 3253 | 3013 | -10845 | -10715 | -11013 | 0 | 239 | 1204 | 55415 | 55909 | 54464
338 | Adriatic HVDC link | PINT | 58 | 79 | 38 | 30 | 35 | 25 | 40 | 54 | 26 | -384 | -316 | -452 | 0 | 8 | 43 | 645 | 826 | 464
339 | Tyrrhenian link | PINT | 53 | 57 | 49 | 17 | 23 | 10 | 70 | 72 | 67 | -214 | -127 | -301 | 0 | 5 | 24 | 1143 | 1185 | 1102
340 | Avelgem-Courcelles (Boucle du Hainaut): new corridor | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341 | North CSE Corridor | PINT | 37 | 39 | 34 | 21 | 24 | 18 | 19 | 20 | 18 | -264 | -233 | -311 | 0 | 6 | 29 | 324 | 353 | 303
342 | Central Balkan Corridor | PINT | 22 | 25 | 19 | 16 | 20 | 11 | 9 | 10 | 7 | -206 | -142 | -259 | 0 | 5 | 23 | 144 | 159 | 125
343 | CSE1 New | PINT | 8 | 14 | 2 | 4 | 4 | 3 | 4 | 6 | 1 | -48 | -36 | -58 | 0 | 1 | 5 | 65 | 105 | 21
346 | ZuidWest380 NL Oost | PINT | 19 | 19 | 19 | 7 | 9 | 5 | 16 | 21 | 12 | -92 | -70 | -113 | 0 | 2 | 10 | 267 | 313 | 219
349 | MaresConnect | PINT | 32 | 32 | 32 | -4 | -4 | -4 | 104 | 104 | 104 | 47 | 47 | 47 | 1 | 0 | 0 | 1833 | 1833 | 1833
350 | South Balkan Corridor | TOOT | 15 | 16 | 13 | 7 | 8 | 6 | 7 | 9 | 5 | -90 | -78 | -105 | 0 | 2 | 10 | 121 | 147 | 90
375 | Lienz (AT) - Veneto region (IT) 220 kV | PINT | 35 | 44 | 27 | 24 | 30 | 16 | 8 | 14 | 3 | -308 | -200 | -384 | 0 | 7 | 34 | 135 | 260 | 51
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | light PINT | 2 | 2 | 2 | 0 | 1 | -1 | 1 | 1 | 0 | -3 | 12 | -15 | 0 | 0 | 0 | 9 | 10 | 7
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | PINT | 20 | 21 | 19 | 7 | 10 | 5 | 18 | 21 | 15 | -95 | -70 | -123 | 0 | 2 | 11 | 311 | 350 | 270
378 | Transformer Gatica | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379 | Uprate Gatica lines | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1034 | HVDC corridor from Northern Germany to Western Germany | PINT | 7182 | 7182 | 7182 | 163 | 163 | 163 | 1202 | 1202 | 1202 | -5819 | -5819 | -5819 | 0 | 128 | 646 | 12027 | 12027 | 12027
1039 | SE North-south long-term reinforcements | light PINT | 19 | 29 | 11 | 8 | 14 | 2 | 1 | 2 | 0 | -105 | -20 | -181 | 0 | 2 | 12 | 118 | 307 | 6
1040 | LirIC | PINT | 50 | 50 | 50 | -4 | -4 | -4 | 81 | 81 | 81 | 51 | 51 | 51 | 1 | 0 | 0 | 1439 | 1439 | 1439
1041 | GREGY Green Energy Interconnector | PINT | 153 | 166 | 136 | 10 | 91 | -86 | 77 | 102 | 59 | -134 | 1099 | -1168 | 0 | 3 | 15 | 1295 | 1556 | 1043
1042 | Offshore Wind LT 1 | PINT | 54 | 59 | 50 | 5 | 7 | 4 | 99 | 104 | 95 | -68 | -47 | -91 | 0 | 1 | 8 | 1650 | 1872 | 1473
1046 | Finnish North-South reinforcement | PINT | 113 | 113 | 113 | 22 | 22 | 22 | 235 | 235 | 235 | -278 | -278 | -278 | 0 | 6 | 31 | 4178 | 4178 | 4178
1047 | Emden-Eemshaven | light PINT | 38 | 46 | 29 | 17 | 22 | 12 | 15 | 18 | 13 | -222 | -149 | -279 | 0 | 5 | 25 | 257 | 312 | 192
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | PINT | 367 | 370 | 364 | 5 | 15 | -9 | 501 | 511 | 492 | -64 | 119 | -192 | 0 | 1 | 7 | 8983 | 9035 | 8889
1049 | Cronos Energy Ltd | PINT | 6 | 6 | 6 | -38 | -38 | -38 | 19 | 19 | 19 | 487 | 487 | 487 | 9 | 0 | 0 | 333 | 333 | 333
1050 | Tarchon Energy Ltd | PINT | 14 | 14 | 14 | -5 | -5 | -5 | 19 | 19 | 19 | 58 | 58 | 58 | 1 | 0 | 0 | 339 | 339 | 339
1051 | Aminth Energy Ltd | PINT | 104 | 104 | 104 | 9 | 9 | 9 | 119 | 119 | 119 | -111 | -111 | -111 | 0 | 2 | 12 | 2109 | 2109 | 2109
1052 | Lienz (AT) - Obersielach (AT) | PINT | 16 | 17 | 13 | 11 | 14 | 10 | 5 | 6 | 3 | -144 | -128 | -173 | 0 | 3 | 16 | 79 | 114 | 60
1054 | Westtirol (AT) - Zell/Ziller (AT) | PINT | 47 | 51 | 40 | 21 | 25 | 19 | 6 | 10 | 3 | -274 | -246 | -321 | 0 | 6 | 30 | 99 | 176 | 58
1055 | Interconnection of Crete to the Mainland System of Greece | TOOT | 264 | 267 | 259 | 70 | 83 | 56 | 260 | 283 | 245 | -902 | -721 | -1069 | 0 | 20 | 100 | 4402 | 4469 | 4308
1058 | HVDC Interconnector DE-CH | light PINT | 85 | 94 | 80 | 51 | 57 | 42 | 15 | 23 | 10 | -651 | -538 | -726 | 0 | 14 | 72 | 259 | 413 | 169
1059 | Southern Italy | PINT | 8 | 13 | 5 | 1 | 1 | -1 | 8 | 11 | 6 | -8 | 10 | -18 | 0 | 0 | 1 | 145 | 205 | 84
1066 | Bulgaria - Turkey | light PINT | 98 | 115 | 84 | -162 | -145 | -173 | 20 | 30 | 11 | 2183 | 2218 | 2147 | 0 | 0 | 0 | 324 | 457 | 206
1067 | New AC 400 kV interconnection line Greece - Turkey | light PINT | 45 | 53 | 36 | -89 | -83 | -95 | 21 | 29 | 16 | 1137 | 1213 | 1059 | 0 | 0 | 0 | 358 | 445 | 281
1068 | LaSGo Link | light PINT | 56 | 56 | 56 | 10 | 11 | 8 | 20 | 24 | 17 | -130 | -107 | -144 | 0 | 3 | 14 | 337 | 361 | 310
1074 | Pannonian Corridor | PINT | 8 | 10 | 5 | 6 | 8 | 5 | 2 | 4 | 1 | -83 | -65 | -103 | 0 | 2 | 9 | 29 | 54 | 15
1082 | Sea-Socket | light PINT | 62 | 78 | 45 | 27 | 28 | 26 | 108 | 109 | 106 | -352 | -333 | -361 | 0 | 8 | 39 | 1915 | 1930 | 1897
1085 | Malta-Italy Cable Link No.2 | PINT | 1 | 2 | 0 | -14 | -13 | -14 | 2 | 3 | 1 | 175 | 185 | 161 | 0 | 0 | 0 | 36 | 52 | 12
1086 | Estonia internal grid reinforcement to increase RES connection capability (RRF project) | PINT | 50 | 56 | 45 | 6 | 9 | 4 | 85 | 86 | 84 | -71 | -51 | -110 | 0 | 2 | 8 | 1419 | 1487 | 1295
1088 | Latvia and Estonia Hybrid Off-Shore interconnector | PINT | 0 | 0 | 0 | 6 | 7 | 5 | 149 | 152 | 146 | -79 | -65 | -94 | 0 | 2 | 9 | 2426 | 2512 | 2341
1092 | Triton Link: offshore hybrid HVDC interconnector Belgium – Denmark | PINT | 252 | 264 | 242 | 188 | 193 | 183 | 693 | 715 | 668 | -2416 | -2352 | -2480 | 0 | 53 | 268 | 12266 | 12382 | 12071
1094 | Estlink 3 | light PINT | 54 | 55 | 53 | 13 | 15 | 11 | 34 | 43 | 29 | -162 | -142 | -190 | 0 | 4 | 18 | 562 | 656 | 513
1095 | Aurora line 2 (4th AC Finland-Sweden north) | light PINT | 48 | 53 | 42 | 6 | 6 | 5 | 47 | 48 | 46 | -75 | -61 | -82 | 0 | 2 | 8 | 787 | 819 | 736
1096 | Beznau - Mettlen | PINT | 32 | 39 | 26 | 15 | 19 | 8 | 10 | 12 | 6 | -194 | -100 | -240 | 0 | 4 | 21 | 165 | 210 | 108
1097 | Upgrade to Konti-Skan | PINT | 113 | 118 | 109 | 42 | 48 | 34 | 37 | 40 | 35 | -540 | -441 | -614 | 0 | 12 | 60 | 627 | 638 | 610
1098 | Offshore Wind LT 2 | PINT | 55 | 59 | 51 | 6 | 7 | 4 | 101 | 103 | 97 | -72 | -57 | -91 | 0 | 2 | 8 | 1651 | 1862 | 1472
1100 | Reinforcement of the existing CZ-DE interconnector (Hradec - Röhrsdorf) on the CZ side | PINT | 16 | 16 | 16 | 7 | 8 | 6 | 7 | 8 | 5 | -88 | -73 | -99 | 0 | 2 | 10 | 123 | 149 | 96
1102 | Mettlen - Ulrichen | light PINT | 8 | 9 | 7 | 4 | 5 | 3 | 1 | 2 | 1 | -54 | -41 | -67 | 0 | 1 | 6 | 23 | 35 | 16
1103 | Bickigen - Chippis | PINT | 20 | 21 | 18 | 12 | 14 | 10 | 5 | 7 | 4 | -155 | -122 | -174 | 0 | 3 | 17 | 85 | 102 | 74
1104 | Niederstedem - Roost | PINT | 0 | 1 | 0 | 1 | 2 | 0 | 2 | 7 | 0 | -11 | 0 | -24 | 0 | 0 | 1 | 39 | 117 | 0
1105 | Georgia-Romania Black Sea (submarine) interconnection cable project | PINT | 40 | 62 | 18 | -8 | -7 | -8 | 32 | 36 | 30 | 96 | 98 | 94 | 0 | 0 | 0 | 540 | 548 | 530
1106 | Bornholm Energy Island (BEI) | TOOT | 165 | 186 | 136 | 159 | 166 | 150 | 455 | 468 | 445 | -2040 | -1920 | -2134 | 0 | 45 | 226 | 8020 | 8044 | 7970
1107 | EuroAfrica Interconnector | PINT | 38 | 42 | 35 | 44 | 45 | 44 | 39 | 51 | 27 | -566 | -560 | -573 | 0 | 12 | 63 | 655 | 783 | 490
1109 | Basilicata - Campania reinforcements | PINT | 9 | 10 | 8 | 2 | 5 | 0 | 12 | 14 | 11 | -30 | 3 | -63 | 0 | 1 | 3 | 203 | 213 | 193
1110 | Sicily - Calabria | PINT | 5 | 8 | 2 | 0 | 2 | -3 | 2 | 3 | 1 | 3 | 33 | -27 | 0 | 0 | 0 | 30 | 42 | 19
1112 | GRITA 2 | PINT | 51 | 55 | 49 | 19 | 21 | 17 | 42 | 45 | 39 | -249 | -220 | -270 | 0 | 5 | 28 | 702 | 730 | 679
1119 | Bisamberg (AT) - Wien SO (AT) - Parndorf (AT) | PINT | 353 | 353 | 353 | 112 | 112 | 112 | 373 | 373 | 373 | -1434 | -1434 | -1434 | 0 | 32 | 159 | 6750 | 6750 | 6750
1120 | Wien SO (AT) – Ternitz (AT) – Hessenberg (AT) | PINT | 87 | 87 | 87 | 29 | 29 | 29 | 95 | 95 | 95 | -374 | -374 | -374 | 0 | 8 | 41 | 1723 | 1723 | 1723
1121 | Hessenberg (AT) - Weißenbach (AT) | PINT | 62 | 62 | 62 | 23 | 23 | 23 | 73 | 73 | 73 | -300 | -300 | -300 | 0 | 7 | 33 | 1310 | 1310 | 1310
1122 | Offshore Wind connection Centre Manche 1 | TOOT | 206 | 220 | 188 | 49 | 51 | 46 | 285 | 290 | 279 | -627 | -593 | -655 | 0 | 14 | 70 | 5156 | 5279 | 5052
1123 | Offshore Wind Connection Centre Manche 2 | PINT | 206 | 220 | 188 | 49 | 51 | 46 | 285 | 290 | 279 | -627 | -593 | -655 | 0 | 14 | 70 | 5156 | 5279 | 5052
1124 | Offshore Wind Connection South Britanny | TOOT | 118 | 135 | 98 | 28 | 31 | 24 | 180 | 198 | 167 | -362 | -309 | -395 | 0 | 8 | 40 | 3042 | 3083 | 3013
1125 | Offshore Wind Connection Occitanie | TOOT | 118 | 135 | 98 | 28 | 31 | 24 | 180 | 198 | 167 | -362 | -309 | -395 | 0 | 8 | 40 | 3042 | 3083 | 3013
1126 | Offshore Wind Connection PACA | TOOT | 118 | 135 | 98 | 28 | 31 | 24 | 180 | 198 | 167 | -362 | -309 | -395 | 0 | 8 | 40 | 3042 | 3083 | 3013
1127 | Offshore Wind Connection South Atlantic | PINT | 203 | 210 | 198 | 49 | 51 | 47 | 295 | 313 | 279 | -628 | -601 | -649 | 0 | 14 | 70 | 5003 | 5190 | 4764
1129 | New RES at Minho region | TOOT | 27 | 33 | 18 | 7 | 8 | 7 | 34 | 38 | 30 | -93 | -85 | -100 | 0 | 2 | 10 | 580 | 633 | 532

## 2040DE-ENTSO-E
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_market_SEW |  |  | ΔRES
|  |  | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | low | mid | high | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year
1 | RES in north of Portugal | TOOT | 76 | 85 | 65 | 11 | 14 | 7 | 66 | 74 | 60 | -93 | -58 | -117 | 3 | 14 | 35 | 1416 | 1579 | 1271
4 | Interconnection Portugal-Spain | TOOT | 37 | 50 | 24 | 6 | 9 | 3 | 29 | 33 | 22 | -52 | -25 | -72 | 2 | 8 | 20 | 620 | 713 | 482
16 | Biscay Gulf | TOOT | 305 | 329 | 272 | 61 | 69 | 52 | 206 | 213 | 199 | -496 | -424 | -560 | 16 | 72 | 186 | 4409 | 4514 | 4337
26 | Reschenpass Interconnector Project | TOOT | 57 | 61 | 51 | 14 | 15 | 11 | 30 | 34 | 25 | -111 | -86 | -125 | 4 | 16 | 42 | 639 | 726 | 526
28 | Italy-Montenegro | PINT | 65 | 99 | 38 | 13 | 20 | 8 | 30 | 43 | 21 | -120 | -85 | -163 | 3 | 15 | 39 | 584 | 730 | 458
29 | Italy-Tunisia | TOOT | 123 | 127 | 119 | -17 | -9 | -24 | 86 | 89 | 82 | 135 | 194 | 76 | 0 | 0 | 0 | 1854 | 1956 | 1753
33 | Central Northern Italy | TOOT | 29 | 42 | 14 | 9 | 11 | 3 | 22 | 23 | 20 | -77 | -46 | -93 | 2 | 10 | 26 | 442 | 506 | 332
35 | CZ Southwest-east corridor | PINT | 44 | 45 | 43 | 6 | 7 | 5 | 34 | 37 | 29 | -52 | -42 | -57 | 2 | 8 | 20 | 721 | 768 | 629
40 | Belgium-Luxembourg-Germany: long-term perspective | light PINT | 53 | 55 | 52 | 11 | 12 | 10 | 33 | 37 | 27 | -92 | -83 | -97 | 3 | 13 | 34 | 695 | 758 | 598
47 | Westtirol (AT) - Vöhringen (DE) | PINT | 67 | 70 | 61 | 16 | 20 | 15 | 35 | 39 | 32 | -152 | -119 | -214 | 4 | 20 | 50 | 706 | 855 | 577
81 | North South Interconnector | TOOT | 153 | 180 | 123 | 47 | 47 | 46 | 70 | 74 | 65 | -381 | -377 | -385 | 13 | 56 | 143 | 1492 | 1562 | 1382
85 | Integration of RES in Alentejo | TOOT | 10 | 15 | 5 | 0 | 3 | -1 | 7 | 10 | 3 | -2 | 11 | -21 | 0 | 0 | 1 | 150 | 207 | 63
94 | GerPol Improvements | TOOT | 219 | 220 | 218 | 81 | 84 | 78 | 102 | 106 | 99 | -661 | -637 | -685 | 22 | 96 | 248 | 2200 | 2230 | 2169
103 | Reinforcements Ring NL phase I | TOOT | 58 | 62 | 54 | 13 | 15 | 9 | 33 | 35 | 29 | -103 | -72 | -119 | 3 | 15 | 39 | 697 | 735 | 631
107 | Celtic Interconnector | TOOT | 208 | 214 | 203 | 37 | 39 | 34 | 102 | 112 | 94 | -302 | -273 | -318 | 10 | 44 | 113 | 2188 | 2387 | 2064
111 | Aurora line (3rd AC Finland-Sweden north) | TOOT | 113 | 119 | 105 | 2 | 3 | 2 | 90 | 105 | 75 | -17 | -12 | -25 | 1 | 3 | 6 | 1916 | 2161 | 1651
120 | Belgian Modular Offshore Grid II (MOG II) | TOOT | 503 | 538 | 467 | 54 | 71 | 33 | 536 | 555 | 525 | -435 | -268 | -579 | 14 | 64 | 163 | 10979 | 11217 | 10857
121 | Nautilus: multi-purpose interconnector Belgium - UK | PINT | 26 | 27 | 24 | -20 | -19 | -22 | 26 | 27 | 25 | 166 | 177 | 154 | 0 | 0 | 0 | 547 | 574 | 521
123 | LitPol Link Stage 2 | TOOT | 168 | 182 | 156 | 83 | 88 | 80 | 48 | 50 | 46 | -675 | -652 | -713 | 22 | 99 | 253 | 1025 | 1036 | 1005
124 | NordBalt phase 2 | PINT | 49 | 56 | 40 | 2 | 4 | -2 | 43 | 53 | 32 | -15 | 15 | -37 | 1 | 2 | 6 | 903 | 1086 | 703
126 | SE North-south short-term reinforcements | TOOT | 88 | 109 | 73 | 14 | 16 | 13 | 55 | 57 | 53 | -114 | -103 | -126 | 4 | 17 | 43 | 1025 | 1232 | 758
127 | Central Southern Italy | TOOT | 34 | 54 | 9 | 3 | 6 | 0 | 41 | 51 | 30 | -26 | -5 | -52 | 1 | 4 | 10 | 809 | 996 | 662
130 | HVDC SuedOstLink Wolmirstedt to area Isar | TOOT | 2107 | 2107 | 2107 | 27 | 27 | 27 | 403 | 403 | 403 | -982 | -982 | -982 | 103 | 455 | 1168 | 4027 | 4027 | 4027
132 | HVDC Line A-North | TOOT | 6300 | 6300 | 6300 | 82 | 82 | 82 | 1146 | 1146 | 1146 | -2935 | -2935 | -2935 | 97 | 429 | 1101 | 11460 | 11460 | 11460
138 | Black Sea Corridor | TOOT | 45 | 52 | 34 | 9 | 13 | 4 | 37 | 41 | 34 | -73 | -34 | -105 | 2 | 11 | 27 | 784 | 851 | 714
142 | CSE4 | TOOT | 35 | 43 | 27 | 8 | 11 | 5 | 24 | 26 | 21 | -61 | -43 | -88 | 2 | 9 | 23 | 503 | 571 | 459
144 | Mid Continental East corridor | TOOT | 92 | 92 | 92 | 17 | 21 | 14 | 72 | 75 | 70 | -135 | -111 | -169 | 4 | 20 | 51 | 1548 | 1588 | 1470
150 | Italy-Slovenia | light PINT | 145 | 155 | 136 | 41 | 43 | 37 | 62 | 66 | 59 | -334 | -303 | -350 | 11 | 49 | 125 | 1338 | 1457 | 1250
153 | France-Alderney-Britain | PINT | 76 | 77 | 76 | 7 | 7 | 7 | 67 | 78 | 53 | -58 | -57 | -59 | 2 | 9 | 22 | 1443 | 1643 | 1158
170 | Baltic States Synchronization with Continental Europe | TOOT | 220 | 221 | 219 | 114 | 120 | 110 | 65 | 69 | 57 | -930 | -892 | -972 | 31 | 136 | 349 | 1395 | 1503 | 1207
174 | Greenconnector | PINT | 128 | 132 | 124 | 34 | 37 | 29 | 47 | 49 | 45 | -277 | -238 | -298 | 9 | 40 | 104 | 1018 | 1084 | 944
176 | Hansa PowerBridge I | TOOT | 163 | 167 | 158 | 33 | 36 | 31 | 97 | 99 | 95 | -272 | -254 | -290 | 9 | 40 | 102 | 2048 | 2124 | 1971
183 | DKW-DE, Westcoast | TOOT | 105 | 122 | 91 | 26 | 28 | 24 | 63 | 67 | 59 | -211 | -194 | -226 | 7 | 31 | 79 | 1334 | 1436 | 1255
186 | East of Austria | TOOT | 132 | 135 | 127 | 16 | 20 | 12 | 136 | 142 | 127 | -132 | -101 | -164 | 4 | 19 | 49 | 2906 | 2999 | 2785
187 | St. Peter (AT) - Pleinting (DE) | PINT | 172 | 175 | 171 | 41 | 47 | 34 | 92 | 95 | 87 | -332 | -275 | -379 | 11 | 49 | 125 | 1941 | 2048 | 1841
190 | NorthConnect | TOOT | 159 | 187 | 125 | 29 | 36 | 22 | 90 | 116 | 56 | -235 | -176 | -296 | 8 | 34 | 88 | 2416 | 3806 | 1205
200 | CZ Northwest-South corridor | TOOT | 45 | 48 | 43 | 7 | 7 | 7 | 33 | 37 | 29 | -57 | -55 | -57 | 2 | 8 | 21 | 704 | 767 | 629
210 | Würmlach (AT) - Somplago (IT) interconnection | TOOT | 33 | 44 | 26 | 8 | 13 | 2 | 14 | 17 | 10 | -67 | -24 | -107 | 2 | 9 | 24 | 299 | 382 | 220
219 | EuroAsia Interconnector | TOOT | 609 | 647 | 570 | 51 | 51 | 51 | 292 | 293 | 291 | -307 | -199 | -414 | 14 | 60 | 155 | 6325 | 6457 | 6193
225 | 2nd interconnector Belgium - Germany | light PINT | 105 | 117 | 94 | 20 | 23 | 15 | 71 | 75 | 68 | -163 | -119 | -188 | 5 | 24 | 61 | 1494 | 1545 | 1448
227 | Transbalkan Corridor | TOOT | 23 | 27 | 20 | 3 | 6 | 1 | 22 | 25 | 16 | -21 | -11 | -48 | 1 | 3 | 8 | 466 | 546 | 344
228 | Muhlbach - Eichstetten | TOOT | 44 | 47 | 38 | 9 | 10 | 7 | 26 | 28 | 24 | -69 | -57 | -78 | 2 | 10 | 26 | 549 | 581 | 514
230 | GerPol Power Bridge I | TOOT | 451 | 456 | 442 | 227 | 230 | 223 | 106 | 108 | 102 | -1843 | -1809 | -1871 | 61 | 269 | 691 | 2250 | 2275 | 2235
231 | Beznau - Tiengen | PINT | 58 | 61 | 56 | 10 | 17 | 7 | 47 | 52 | 38 | -85 | -56 | -141 | 3 | 12 | 32 | 992 | 1084 | 836
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Bergrheinfeld West | TOOT | 7723 | 7723 | 7723 | 105 | 105 | 105 | 1407 | 1407 | 1407 | -3738 | -3738 | -3838 | 33 | 145 | 371 | 14075 | 14075 | 14075
239 | Fenno-Skan 1 renewal | light PINT | 50 | 55 | 43 | -1 | 1 | -5 | 41 | 42 | 40 | 6 | 39 | -10 | 0 | 0 | 0 | 986 | 1175 | 883
243 | New 400 kV interconnection line between Serbia and Croatia | light PINT | 10 | 13 | 6 | 1 | 2 | 0 | 5 | 7 | 3 | -9 | -1 | -20 | 0 | 1 | 3 | 106 | 138 | 66
244 | Vigy - Uchtelfangen area | PINT | 230 | 236 | 224 | 46 | 50 | 40 | 137 | 143 | 134 | -374 | -327 | -405 | 12 | 55 | 140 | 2837 | 2956 | 2682
247 | AQUIND Interconnector | PINT | 106 | 120 | 91 | 11 | 13 | 9 | 96 | 114 | 78 | -92 | -74 | -105 | 3 | 13 | 34 | 2043 | 2416 | 1717
250 | Merchant line Castasegna (CH) - Mese (IT) | PINT | 16 | 24 | 11 | 5 | 11 | 0 | 8 | 8 | 7 | -38 | -4 | -93 | 1 | 6 | 14 | 155 | 172 | 136
252 | Internal Belgian Backbone Center-East: HTLS upgrade Massenhoven-VanEyck-Gramme-Courcelles-Bruegel-Mercator | PINT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253 | Upstream reinforcement in France to increase FR-CH capacity | PINT | 51 | 57 | 46 | 14 | 16 | 12 | 20 | 29 | 14 | -113 | -99 | -129 | 4 | 17 | 42 | 330 | 419 | 233
254 | HVDC Ultranet Osterath to Philippsburg | TOOT | 783 | 783 | 783 | 6 | 6 | 6 | 221 | 221 | 221 | -200 | -200 | -200 | 97 | 431 | 1107 | 2211 | 2211 | 2211
259 | HU-RO | PINT | 69 | 76 | 66 | 10 | 12 | 8 | 48 | 51 | 46 | -79 | -64 | -97 | 3 | 12 | 30 | 1022 | 1062 | 978
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | PINT | 38 | 50 | 26 | -19 | -11 | -26 | 29 | 36 | 19 | 158 | 207 | 88 | 0 | 0 | 0 | 620 | 769 | 412
263 | Lake Constance East | light PINT | 155 | 167 | 147 | 38 | 44 | 33 | 73 | 78 | 71 | -310 | -268 | -354 | 10 | 45 | 116 | 1575 | 1707 | 1507
267 | Hansa PowerBridge II | light PINT | 147 | 147 | 147 | 29 | 30 | 27 | 71 | 86 | 56 | -238 | -223 | -248 | 8 | 35 | 89 | 1511 | 1786 | 1236
270 | FR-ES project -Aragón-Atlantic Pyrenees | PINT | 183 | 185 | 178 | 37 | 41 | 34 | 139 | 141 | 135 | -302 | -275 | -331 | 10 | 44 | 113 | 2977 | 2990 | 2963
276 | FR-ES project -Navarra-Landes | PINT | 183 | 185 | 178 | 37 | 41 | 34 | 139 | 141 | 135 | -302 | -275 | -331 | 10 | 44 | 113 | 2977 | 2990 | 2963
280 | FR-BE: study Lonny-Achene-Gramme | PINT | 128 | 138 | 120 | 31 | 35 | 27 | 54 | 58 | 51 | -255 | -223 | -284 | 8 | 37 | 96 | 1163 | 1224 | 1116
283 | TuNur Italy | PINT | 19 | 50 | 0 | 39 | 80 | -1 | 0 | 0 | 0 | -314 | 10 | -653 | 10 | 46 | 118 | -1523 | 0 | -4570
285 | GridLink | PINT | 76 | 77 | 76 | 7 | 7 | 7 | 67 | 78 | 53 | -58 | -57 | -59 | 2 | 9 | 22 | 1443 | 1643 | 1158
286 | Greenlink | PINT | 22 | 25 | 19 | 16 | 17 | 16 | 39 | 46 | 35 | -133 | -130 | -139 | 4 | 19 | 50 | 820 | 1010 | 739
293 | Southern Aegean Interconnector | PINT | 24 | 28 | 22 | 4 | 7 | 1 | 26 | 29 | 21 | -34 | -8 | -60 | 1 | 5 | 13 | 541 | 622 | 454
297 | BRABO II + III | TOOT | 34 | 35 | 33 | 4 | 8 | 1 | 22 | 23 | 21 | -37 | -9 | -62 | 1 | 5 | 14 | 481 | 512 | 453
299 | SACOI3 | TOOT | 92 | 102 | 80 | 27 | 30 | 22 | 41 | 42 | 41 | -223 | -180 | -247 | 7 | 33 | 84 | 889 | 899 | 881
309 | NeuConnect | TOOT | 56 | 61 | 53 | 10 | 15 | 5 | 68 | 78 | 51 | -79 | -40 | -125 | 3 | 12 | 30 | 1637 | 1666 | 1608
312 | St. Peter (AT) - Tauern (AT) | TOOT | 237 | 243 | 226 | 53 | 59 | 49 | 129 | 130 | 126 | -432 | -396 | -479 | 14 | 63 | 162 | 2736 | 2855 | 2644
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | TOOT | 238 | 243 | 226 | 55 | 62 | 49 | 128 | 130 | 126 | -447 | -396 | -503 | 15 | 65 | 167 | 2708 | 2855 | 2596
323 | Dekani (SI) - Zaule (IT) interconnection | TOOT | 6 | 9 | 2 | 2 | 4 | 0 | 3 | 6 | 0 | -17 | -1 | -30 | 1 | 2 | 6 | 68 | 127 | 6
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | TOOT | 5 | 11 | 1 | 0 | 1 | -3 | 5 | 14 | 0 | 1 | 22 | -11 | 0 | 0 | 0 | 106 | 304 | 7
325 | Obersielach (AT) - Podlog (SI) | PINT | 40 | 47 | 32 | 3 | 6 | 0 | 24 | 30 | 21 | -25 | 7 | -48 | 1 | 4 | 10 | 507 | 647 | 347
328 | Interconnector DE-LUX | TOOT | 6 | 10 | 2 | 1 | 1 | 0 | 3 | 8 | 0 | -7 | -2 | -11 | 0 | 1 | 2 | 64 | 172 | -38
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
330 | 4th 400kV CZ-SK interconnector | light PINT | 29 | 32 | 24 | 6 | 7 | 6 | 18 | 25 | 11 | -49 | -45 | -55 | 2 | 7 | 18 | 380 | 511 | 246
333 | PST Foretaille | PINT | 113 | 114 | 111 | 27 | 29 | 25 | 53 | 57 | 46 | -222 | -199 | -237 | 7 | 32 | 83 | 1134 | 1199 | 1027
335 | North Sea Wind Power Hub | light PINT | 228 | 265 | 203 | 278 | 286 | 266 | 1654 | 1668 | 1640 | -2262 | -2163 | -2327 | 75 | 330 | 848 | 34708 | 34855 | 34486
338 | Adriatic HVDC link | PINT | 147 | 180 | 121 | 38 | 40 | 35 | 75 | 83 | 65 | -273 | -208 | -323 | 10 | 45 | 115 | 1340 | 1385 | 1294
339 | Tyrrhenian link | PINT | 98 | 104 | 92 | 12 | 16 | 9 | 104 | 110 | 97 | -117 | -93 | -130 | 3 | 14 | 37 | 2452 | 2869 | 2137
340 | Avelgem-Courcelles (Boucle du Hainaut): new corridor | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341 | North CSE Corridor | PINT | 46 | 49 | 42 | 5 | 10 | 0 | 40 | 47 | 35 | -44 | 1 | -82 | 1 | 6 | 17 | 806 | 871 | 741
342 | Central Balkan Corridor | PINT | 46 | 48 | 45 | 5 | 6 | 4 | 45 | 49 | 40 | -43 | -32 | -52 | 1 | 6 | 16 | 974 | 1044 | 849
343 | CSE1 New | PINT | 6 | 11 | 3 | 0 | 2 | -2 | 3 | 3 | 3 | -2 | 20 | -16 | 0 | 0 | 1 | 63 | 74 | 54
346 | ZuidWest380 NL Oost | PINT | 34 | 35 | 33 | 4 | 8 | 1 | 22 | 23 | 21 | -37 | -9 | -62 | 1 | 5 | 14 | 481 | 512 | 453
349 | MaresConnect | PINT | 42 | 53 | 34 | 22 | 23 | 20 | 55 | 60 | 51 | -176 | -166 | -183 | 6 | 26 | 66 | 1181 | 1310 | 1067
350 | South Balkan Corridor | TOOT | 23 | 26 | 20 | 3 | 6 | 1 | 23 | 24 | 21 | -25 | -10 | -48 | 1 | 4 | 9 | 485 | 517 | 436
375 | Lienz (AT) - Veneto region (IT) 220 kV | PINT | 98 | 104 | 92 | 26 | 28 | 22 | 53 | 56 | 51 | -210 | -183 | -228 | 7 | 31 | 79 | 1011 | 1235 | 718
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | light PINT | 6 | 10 | 1 | 0 | 1 | -1 | 5 | 5 | 4 | -4 | 7 | -11 | 0 | 1 | 2 | 101 | 114 | 89
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | PINT | 35 | 36 | 34 | 6 | 8 | 5 | 22 | 23 | 21 | -47 | -38 | -62 | 2 | 7 | 18 | 471 | 512 | 448
378 | Transformer Gatica | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379 | Uprate Gatica lines | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1034 | HVDC corridor from Northern Germany to Western Germany | PINT | 7513 | 7513 | 7513 | 105 | 105 | 105 | 1422 | 1422 | 1422 | -3749 | -3749 | -3749 | 53 | 235 | 604 | 14224 | 14224 | 14224
1039 | SE North-south long-term reinforcements | light PINT | 18 | 19 | 17 | 5 | 8 | 3 | 11 | 15 | 8 | -41 | -25 | -65 | 1 | 6 | 15 | 245 | 313 | 185
1040 | LirIC | PINT | 65 | 74 | 60 | 15 | 16 | 14 | 21 | 24 | 18 | -123 | -112 | -129 | 4 | 18 | 46 | 457 | 504 | 377
1041 | GREGY Green Energy Interconnector | PINT | 746 | 767 | 731 | -47 | -9 | -114 | 438 | 458 | 427 | 379 | 924 | 73 | 0 | 0 | 0 | 9415 | 10095 | 9063
1042 | Offshore Wind LT 1 | PINT | 30 | 39 | 22 | 1 | 2 | 0 | 36 | 47 | 31 | -10 | 1 | -17 | 0 | 1 | 4 | 779 | 982 | 641
1046 | Finnish North-South reinforcement | PINT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1047 | Emden-Eemshaven | light PINT | 90 | 109 | 77 | 16 | 18 | 13 | 52 | 56 | 48 | -128 | -105 | -144 | 4 | 19 | 48 | 1122 | 1183 | 1053
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | PINT | 610 | 628 | 595 | -10 | -2 | -19 | 475 | 487 | 465 | 82 | 154 | 13 | 0 | 0 | 0 | 10150 | 10269 | 9891
1049 | Cronos Energy Ltd | PINT | 32 | 33 | 31 | -12 | -5 | -16 | 5 | 13 | 1 | 97 | 130 | 39 | 0 | 0 | 0 | 108 | 270 | 16
1050 | Tarchon Energy Ltd | PINT | 54 | 70 | 43 | 9 | 10 | 8 | 59 | 70 | 42 | -76 | -64 | -85 | 3 | 11 | 29 | 1254 | 1482 | 929
1051 | Aminth Energy Ltd | PINT | 81 | 98 | 63 | 13 | 14 | 12 | 94 | 99 | 90 | -107 | -101 | -113 | 4 | 16 | 40 | 2023 | 2085 | 1985
1052 | Lienz (AT) - Obersielach (AT) | PINT | 49 | 54 | 43 | 6 | 8 | 5 | 41 | 48 | 32 | -52 | -42 | -68 | 2 | 8 | 20 | 881 | 1009 | 702
1054 | Westtirol (AT) - Zell/Ziller (AT) | PINT | 66 | 68 | 61 | 16 | 18 | 15 | 37 | 41 | 33 | -134 | -119 | -148 | 4 | 20 | 50 | 785 | 871 | 674
1055 | Interconnection of Crete to the Mainland System of Greece | TOOT | 174 | 181 | 165 | 12 | 14 | 10 | 131 | 143 | 117 | -95 | -85 | -112 | 3 | 14 | 36 | 2808 | 3049 | 2576
1058 | HVDC Interconnector DE-CH | light PINT | 133 | 145 | 124 | 28 | 31 | 24 | 73 | 76 | 69 | -231 | -192 | -254 | 8 | 34 | 87 | 1562 | 1612 | 1531
1059 | Southern Italy | PINT | 7 | 9 | 5 | 0 | 1 | -2 | 8 | 12 | 1 | 4 | 18 | -7 | 0 | 0 | 0 | 151 | 263 | 15
1066 | Bulgaria - Turkey | light PINT | 263 | 269 | 258 | -19 | -17 | -22 | 137 | 152 | 126 | 157 | 175 | 138 | 0 | 0 | 0 | 2961 | 3344 | 2676
1067 | New AC 400 kV interconnection line Greece - Turkey | light PINT | 163 | 181 | 151 | -12 | -7 | -15 | 93 | 101 | 83 | 95 | 123 | 58 | 0 | 0 | 0 | 1998 | 2218 | 1768
1068 | LaSGo Link | light PINT | 49 | 60 | 40 | 4 | 9 | 0 | 31 | 33 | 28 | -28 | 4 | -75 | 1 | 4 | 11 | 658 | 704 | 608
1074 | Pannonian Corridor | PINT | 18 | 22 | 15 | 5 | 6 | 4 | 13 | 17 | 10 | -41 | -35 | -52 | 1 | 6 | 15 | 283 | 361 | 218
1082 | Sea-Socket | light PINT | 68 | 75 | 62 | 9 | 10 | 9 | 74 | 75 | 73 | -74 | -70 | -82 | 2 | 11 | 28 | 1580 | 1594 | 1555
1085 | Malta-Italy Cable Link No.2 | PINT | 0 | 0 | 0 | -7 | -7 | -7 | 3 | 5 | 1 | 57 | 59 | 55 | 0 | 0 | 0 | 58 | 101 | 23
1086 | Estonia internal grid reinforcement to increase RES connection capability (RRF project) | PINT | 35 | 38 | 33 | 1 | 1 | 1 | 34 | 38 | 28 | -9 | -9 | -10 | 0 | 1 | 3 | 715 | 788 | 581
1088 | Latvia and Estonia Hybrid Off-Shore interconnector | PINT | 0 | 0 | 0 | 2 | 2 | 1 | 60 | 63 | 56 | -13 | -10 | -14 | 0 | 2 | 5 | 1251 | 1336 | 1186
1092 | Triton Link: offshore hybrid HVDC interconnector Belgium – Denmark | PINT | 337 | 340 | 334 | 84 | 86 | 81 | 439 | 449 | 432 | -682 | -662 | -701 | 22 | 100 | 256 | 9208 | 9287 | 9120
1094 | Estlink 3 | light PINT | 40 | 42 | 37 | 4 | 5 | 3 | 31 | 37 | 28 | -34 | -28 | -41 | 1 | 5 | 13 | 667 | 763 | 595
1095 | Aurora line 2 (4th AC Finland-Sweden north) | light PINT | 96 | 97 | 95 | -2 | 1 | -5 | 58 | 60 | 55 | 15 | 39 | -12 | 0 | 0 | 0 | 1252 | 1285 | 1220
1096 | Beznau - Mettlen | PINT | 80 | 91 | 63 | 15 | 22 | 10 | 54 | 59 | 49 | -124 | -81 | -182 | 4 | 18 | 46 | 1155 | 1250 | 1090
1097 | Upgrade to Konti-Skan | PINT | 68 | 71 | 65 | 13 | 16 | 10 | 46 | 47 | 45 | -108 | -85 | -132 | 4 | 16 | 41 | 990 | 994 | 986
1098 | Offshore Wind LT 2 | PINT | 30 | 33 | 22 | 1 | 2 | 0 | 32 | 33 | 31 | -10 | 1 | -17 | 0 | 2 | 4 | 685 | 698 | 668
1100 | Reinforcement of the existing CZ-DE interconnector (Hradec - Röhrsdorf) on the CZ side | PINT | 27 | 30 | 23 | 2 | 3 | 0 | 28 | 37 | 17 | -15 | 3 | -26 | 0 | 2 | 6 | 601 | 794 | 374
1102 | Mettlen - Ulrichen | light PINT | 21 | 25 | 15 | 3 | 6 | 1 | 16 | 18 | 13 | -28 | -7 | -50 | 1 | 4 | 11 | 340 | 389 | 282
1103 | Bickigen - Chippis | PINT | 56 | 64 | 51 | 11 | 16 | 8 | 36 | 40 | 34 | -89 | -65 | -129 | 3 | 13 | 33 | 778 | 818 | 757
1104 | Niederstedem - Roost | PINT | 2 | 4 | 0 | 1 | 3 | 0 | 1 | 3 | 0 | -7 | 0 | -21 | 0 | 1 | 3 | 24 | 57 | 1
1105 | Georgia-Romania Black Sea (submarine) interconnection cable project | PINT | 84 | 127 | 21 | 15 | 18 | 13 | 42 | 101 | 3 | -105 | -103 | -108 | 4 | 17 | 45 | 981 | 2215 | 68
1106 | Bornholm Energy Island (BEI) | TOOT | 90 | 125 | 68 | 37 | 41 | 29 | 245 | 285 | 224 | -298 | -238 | -335 | 10 | 43 | 112 | 5161 | 6071 | 4685
1107 | EuroAfrica Interconnector | PINT | 107 | 107 | 107 | 4 | 9 | -3 | 31 | 35 | 24 | -31 | 28 | -73 | 1 | 4 | 12 | 659 | 753 | 516
1109 | Basilicata - Campania reinforcements | PINT | 7 | 11 | 0 | -1 | 0 | -2 | 16 | 21 | 10 | 5 | 13 | 0 | 0 | 0 | 0 | 309 | 351 | 230
1110 | Sicily - Calabria | PINT | 3 | 4 | 2 | 0 | 1 | -3 | 5 | 6 | 5 | 2 | 22 | -10 | 0 | 0 | 0 | 110 | 130 | 77
1112 | GRITA 2 | PINT | 62 | 66 | 56 | 9 | 14 | 1 | 40 | 49 | 32 | -75 | -15 | -114 | 2 | 11 | 28 | 798 | 910 | 700
1119 | Bisamberg (AT) - Wien SO (AT) - Parndorf (AT) | PINT | 134 | 134 | 134 | 25 | 25 | 25 | 154 | 154 | 154 | -204 | -204 | -204 | 7 | 30 | 76 | 3248 | 3248 | 3248
1120 | Wien SO (AT) – Ternitz (AT) – Hessenberg (AT) | PINT | 35 | 35 | 35 | 7 | 7 | 7 | 34 | 34 | 34 | -61 | -61 | -61 | 2 | 9 | 23 | 718 | 718 | 718
1121 | Hessenberg (AT) - Weißenbach (AT) | PINT | 22 | 22 | 22 | 3 | 3 | 3 | 29 | 29 | 29 | -26 | -26 | -26 | 1 | 4 | 10 | 603 | 603 | 603
1122 | Offshore Wind connection Centre Manche 1 | TOOT | 135 | 137 | 133 | 13 | 15 | 11 | 164 | 169 | 157 | -106 | -92 | -126 | 3 | 15 | 40 | 3521 | 3584 | 3449
1123 | Offshore Wind Connection Centre Manche 2 | PINT | 135 | 137 | 133 | 13 | 15 | 11 | 164 | 169 | 157 | -106 | -92 | -126 | 3 | 15 | 40 | 3521 | 3584 | 3449
1124 | Offshore Wind Connection South Britanny | TOOT | 83 | 85 | 80 | 8 | 8 | 7 | 99 | 101 | 95 | -62 | -57 | -68 | 2 | 9 | 23 | 2132 | 2156 | 2094
1125 | Offshore Wind Connection Occitanie | TOOT | 83 | 85 | 80 | 8 | 8 | 7 | 99 | 101 | 95 | -62 | -57 | -68 | 2 | 9 | 23 | 2132 | 2156 | 2094
1126 | Offshore Wind Connection PACA | TOOT | 83 | 85 | 80 | 8 | 8 | 7 | 99 | 101 | 95 | -62 | -57 | -68 | 2 | 9 | 23 | 2132 | 2156 | 2094
1127 | Offshore Wind Connection South Atlantic | PINT | 137 | 137 | 136 | 13 | 15 | 11 | 164 | 169 | 157 | -106 | -92 | -126 | 4 | 16 | 40 | 3520 | 3580 | 3449
1129 | New RES at Minho region | TOOT | 22 | 27 | 20 | 1 | 2 | -2 | 23 | 27 | 20 | -4 | 17 | -20 | 0 | 1 | 2 | 484 | 572 | 435

## 2030DEGS-ENTSO-E
| Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_market_SEW |  |  | ΔRES |  |  | ΔRES_MW
|  |  | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | low | mid | high | weighted avg | max | min | Explicit
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW
1 | RES in north of Portugal | TOOT | 96 | 101 | 87 | 24 | 28 | 17 | 73 | 75 | 70 | -308 | -220 | -355 | 0 | 7 | 34 | 933 | 978 | 888
4 | Interconnection Portugal-Spain | TOOT | 35 | 48 | 25 | 10 | 16 | 5 | 19 | 29 | 9 | -129 | -58 | -202 | 0 | 3 | 14 | 240 | 363 | 110
16 | Biscay Gulf | TOOT | 480 | 488 | 470 | 106 | 120 | 89 | 415 | 433 | 402 | -1353 | -1144 | -1542 | 0 | 30 | 150 | 5348 | 5478 | 5241
26 | Reschenpass Interconnector Project | TOOT | 42 | 72 | 19 | 14 | 18 | 10 | 8 | 14 | 5 | -182 | -135 | -227 | 0 | 4 | 20 | 103 | 170 | 68
28 | Italy-Montenegro | PINT | 49 | 51 | 47 | 15 | 16 | 13 | 26 | 35 | 21 | -195 | -172 | -227 | 0 | 4 | 21 | 338 | 437 | 271
29 | Italy-Tunisia | TOOT | 88 | 110 | 63 | -75 | -64 | -89 | 72 | 74 | 71 | 1002 | 1270 | 818 | 17 | 0 | 0 | 854 | 936 | 701
33 | Central Northern Italy | TOOT | 38 | 40 | 37 | 13 | 17 | 11 | 24 | 32 | 16 | -172 | -135 | -213 | 0 | 4 | 18 | 305 | 407 | 211
35 | CZ Southwest-east corridor | PINT | 55 | 89 | 24 | 7 | 14 | 3 | 8 | 11 | 6 | -95 | -38 | -181 | 0 | 2 | 11 | 116 | 149 | 76
40 | Belgium-Luxembourg-Germany: long-term perspective | light PINT | 36 | 38 | 33 | 7 | 8 | 7 | 7 | 8 | 6 | -92 | -85 | -99 | 0 | 2 | 10 | 101 | 104 | 97
47 | Westtirol (AT) - Vöhringen (DE) | PINT | 60 | 71 | 51 | 16 | 22 | 9 | 7 | 17 | 4 | -215 | -117 | -321 | 0 | 5 | 23 | 96 | 217 | 46
81 | North South Interconnector | TOOT | 93 | 105 | 77 | 21 | 25 | 15 | 29 | 36 | 22 | -271 | -196 | -316 | 0 | 6 | 30 | 374 | 467 | 282
85 | Integration of RES in Alentejo | TOOT | 16 | 24 | 8 | 3 | 7 | 0 | 39 | 42 | 37 | -33 | 5 | -86 | 0 | 1 | 4 | 505 | 552 | 478
94 | GerPol Improvements | TOOT | 197 | 209 | 186 | 37 | 40 | 34 | 62 | 70 | 53 | -475 | -438 | -512 | 0 | 10 | 53 | 790 | 884 | 696
103 | Reinforcements Ring NL phase I | TOOT | 47 | 48 | 46 | 7 | 11 | 4 | 12 | 16 | 7 | -89 | -55 | -135 | 0 | 2 | 10 | 163 | 200 | 87
107 | Celtic Interconnector | TOOT | 103 | 111 | 95 | 34 | 35 | 32 | 146 | 147 | 144 | -430 | -405 | -455 | 0 | 9 | 48 | 1900 | 1915 | 1886
111 | Aurora line (3rd AC Finland-Sweden north) | TOOT | 86 | 90 | 80 | 7 | 8 | 6 | 74 | 74 | 74 | -91 | -80 | -108 | 0 | 2 | 10 | 1148 | 1275 | 966
120 | Belgian Modular Offshore Grid II (MOG II) | TOOT | 1013 | 1015 | 1012 | 246 | 253 | 241 | 1137 | 1163 | 1111 | -3159 | -3088 | -3245 | 0 | 70 | 351 | 14658 | 14738 | 14534
121 | Nautilus: multi-purpose interconnector Belgium - UK | PINT | 0 | 0 | 0 | -69 | -39 | -99 | 22 | 25 | 18 | 885 | 1266 | 503 | 16 | 0 | 0 | 279 | 320 | 238
123 | LitPol Link Stage 2 | TOOT | 234 | 237 | 231 | 146 | 154 | 136 | 62 | 73 | 48 | -1873 | -1745 | -1971 | 0 | 41 | 208 | 865 | 963 | 807
124 | NordBalt phase 2 | PINT | 56 | 63 | 46 | 15 | 17 | 11 | 32 | 36 | 23 | -189 | -141 | -216 | 0 | 4 | 21 | 439 | 471 | 400
126 | SE North-south short-term reinforcements | TOOT | 140 | 141 | 139 | 26 | 32 | 20 | 62 | 69 | 55 | -330 | -259 | -406 | 0 | 7 | 37 | 917 | 950 | 884
127 | Central Southern Italy | TOOT | 46 | 65 | 24 | 16 | 22 | 8 | 67 | 70 | 60 | -214 | -101 | -277 | 0 | 5 | 23 | 805 | 905 | 649
130 | HVDC SuedOstLink Wolmirstedt to area Isar | TOOT | 2174 | 2174 | 2174 | 41 | 41 | 41 | 371 | 371 | 371 | -1478 | -1478 | -1478 | 0 | 33 | 164 | 3718 | 3718 | 3718
132 | HVDC Line A-North | TOOT | 5249 | 5249 | 5249 | 129 | 129 | 129 | 853 | 853 | 853 | -4603 | -4603 | -4603 | 0 | 101 | 511 | 8531 | 8531 | 8531
138 | Black Sea Corridor | TOOT | 76 | 78 | 73 | 17 | 22 | 11 | 27 | 36 | 18 | -224 | -142 | -288 | 0 | 5 | 25 | 362 | 449 | 307
142 | CSE4 | TOOT | 25 | 34 | 16 | -10 | -4 | -19 | 13 | 16 | 9 | 134 | 246 | 54 | 2 | 0 | 0 | 178 | 204 | 163
144 | Mid Continental East corridor | TOOT | 158 | 160 | 156 | 83 | 88 | 74 | 78 | 80 | 75 | -1060 | -943 | -1130 | 0 | 23 | 118 | 1003 | 1046 | 981
150 | Italy-Slovenia | light PINT | 87 | 107 | 65 | 0 | 5 | -7 | 14 | 20 | 11 | -1 | 86 | -66 | 0 | 0 | 0 | 187 | 262 | 141
153 | France-Alderney-Britain | PINT | 0 | 0 | 0 | -38 | -33 | -42 | 28 | 38 | 17 | 483 | 545 | 417 | 9 | 0 | 0 | 358 | 492 | 210
170 | Baltic States Synchronization with Continental Europe | TOOT | 306 | 332 | 288 | 207 | 219 | 196 | 91 | 92 | 90 | -2654 | -2517 | -2803 | 0 | 58 | 295 | 1261 | 1444 | 1165
174 | Greenconnector | PINT | 88 | 110 | 63 | 11 | 15 | 7 | 7 | 9 | 4 | -185 | -103 | -312 | 0 | 3 | 16 | 93 | 122 | 52
176 | Hansa PowerBridge I | TOOT | 359 | 360 | 358 | 138 | 141 | 134 | 76 | 82 | 69 | -1763 | -1721 | -1806 | 0 | 39 | 196 | 1114 | 1193 | 1036
183 | DKW-DE, Westcoast | TOOT | 321 | 327 | 315 | 130 | 134 | 126 | 135 | 149 | 121 | -1668 | -1616 | -1720 | 0 | 37 | 185 | 1986 | 2077 | 1895
186 | East of Austria | TOOT | 416 | 423 | 409 | 129 | 144 | 111 | 448 | 454 | 441 | -1723 | -1427 | -2060 | 0 | 36 | 183 | 5830 | 5897 | 5760
187 | St. Peter (AT) - Pleinting (DE) | PINT | 145 | 162 | 136 | 36 | 49 | 24 | 9 | 15 | 7 | -422 | -301 | -567 | 0 | 10 | 51 | 129 | 190 | 89
190 | NorthConnect | TOOT | 91 | 132 | 32 | 72 | 72 | 71 | 100 | 189 | 53 | -920 | -913 | -926 | 0 | 20 | 102 | 1383 | 2496 | 679
200 | CZ Northwest-South corridor | TOOT | 62 | 73 | 46 | 10 | 16 | 2 | 10 | 13 | 8 | -126 | -31 | -208 | 0 | 3 | 14 | 145 | 174 | 130
210 | Würmlach (AT) - Somplago (IT) interconnection | TOOT | 8 | 12 | 4 | 4 | 9 | 0 | 2 | 4 | 1 | -49 | 3 | -109 | 0 | 1 | 5 | 26 | 52 | 7
219 | EuroAsia Interconnector | TOOT | 673 | 683 | 662 | 3 | 23 | -17 | 419 | 427 | 410 | -36 | 224 | -295 | 0 | 1 | 4 | 5385 | 5581 | 5189
225 | 2nd interconnector Belgium - Germany | light PINT | 86 | 90 | 83 | 8 | 13 | 3 | 17 | 20 | 10 | -104 | -34 | -165 | 0 | 2 | 11 | 228 | 256 | 180
227 | Transbalkan Corridor | TOOT | 43 | 49 | 36 | -6 | -2 | -11 | 21 | 30 | 16 | 79 | 137 | 31 | 1 | 0 | 0 | 294 | 373 | 229
228 | Muhlbach - Eichstetten | TOOT | 56 | 61 | 54 | 21 | 27 | 15 | 6 | 7 | 5 | -273 | -195 | -349 | 0 | 6 | 30 | 81 | 94 | 62
230 | GerPol Power Bridge I | TOOT | 310 | 312 | 307 | 200 | 202 | 196 | 35 | 45 | 27 | -2560 | -2508 | -2592 | 0 | 56 | 284 | 486 | 566 | 433
231 | Beznau - Tiengen | PINT | 55 | 57 | 50 | 15 | 21 | 7 | 9 | 11 | 6 | -196 | -91 | -265 | 0 | 4 | 22 | 128 | 143 | 102
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Bergrheinfeld West | TOOT | 9783 | 9783 | 9783 | 248 | 248 | 248 | 1668 | 1668 | 1668 | -8869 | -8869 | -8869 | 0 | 195 | 984 | 16684 | 16684 | 16684
239 | Fenno-Skan 1 renewal | light PINT | 29 | 33 | 23 | 3 | 6 | 2 | 40 | 51 | 28 | -42 | -20 | -74 | 0 | 1 | 5 | 549 | 666 | 478
243 | New 400 kV interconnection line between Serbia and Croatia | light PINT | 14 | 18 | 11 | 5 | 9 | 1 | 2 | 5 | 0 | -68 | -8 | -113 | 0 | 1 | 8 | 29 | 64 | 1
244 | Vigy - Uchtelfangen area | PINT | 289 | 300 | 272 | 92 | 103 | 83 | 32 | 39 | 24 | -1185 | -1067 | -1324 | 0 | 26 | 132 | 436 | 505 | 382
247 | AQUIND Interconnector | PINT | 0 | 0 | 0 | -51 | -34 | -67 | 32 | 37 | 23 | 655 | 853 | 436 | 12 | 0 | 0 | 413 | 474 | 296
250 | Merchant line Castasegna (CH) - Mese (IT) | PINT | 19 | 25 | 13 | 3 | 8 | 1 | 2 | 4 | 1 | -37 | -12 | -97 | 0 | 1 | 4 | 28 | 46 | 19
252 | Internal Belgian Backbone Center-East: HTLS upgrade Massenhoven-VanEyck-Gramme-Courcelles-Bruegel-Mercator | PINT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253 | Upstream reinforcement in France to increase FR-CH capacity | PINT | 52 | 64 | 43 | 13 | 18 | 8 | 3 | 4 | 3 | -171 | -104 | -229 | 0 | 4 | 19 | 44 | 49 | 36
254 | HVDC Ultranet Osterath to Philippsburg | TOOT | 1683 | 1683 | 1683 | 38 | 38 | 38 | 300 | 300 | 300 | -1366 | -1366 | -1366 | 0 | 30 | 152 | 2996 | 2996 | 2996
259 | HU-RO | PINT | 70 | 79 | 63 | 25 | 28 | 21 | 28 | 31 | 22 | -327 | -273 | -358 | 0 | 7 | 36 | 391 | 407 | 378
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | PINT | 0 | 0 | 0 | -62 | -10 | -117 | 28 | 31 | 24 | 792 | 1494 | 127 | 14 | 0 | 0 | 362 | 408 | 315
263 | Lake Constance East | light PINT | 141 | 167 | 111 | 32 | 36 | 28 | 16 | 21 | 14 | -414 | -360 | -464 | 0 | 9 | 46 | 212 | 266 | 183
267 | Hansa PowerBridge II | light PINT | 316 | 317 | 314 | 125 | 125 | 124 | 64 | 67 | 60 | -1597 | -1596 | -1597 | 0 | 35 | 177 | 946 | 1038 | 854
270 | FR-ES project -Aragón-Atlantic Pyrenees | PINT | 273 | 277 | 268 | 61 | 66 | 56 | 242 | 244 | 240 | -778 | -714 | -841 | 0 | 17 | 86 | 3119 | 3186 | 3042
276 | FR-ES project -Navarra-Landes | PINT | 273 | 277 | 268 | 61 | 66 | 56 | 242 | 244 | 240 | -778 | -714 | -841 | 0 | 17 | 86 | 3119 | 3186 | 3042
280 | FR-BE: study Lonny-Achene-Gramme | PINT | 144 | 153 | 131 | 41 | 44 | 36 | 8 | 10 | 6 | -529 | -467 | -567 | 0 | 12 | 59 | 108 | 124 | 80
283 | TuNur Italy | PINT | 3 | 31 | -22 | 147 | 230 | 64 | 493 | 990 | 0 | -1912 | -816 | -2945 | 0 | 41 | 209 | 6395 | 12835 | 0
285 | GridLink | PINT | 0 | 0 | 0 | -38 | -33 | -44 | 30 | 38 | 25 | 488 | 560 | 417 | 9 | 0 | 0 | 392 | 492 | 314
286 | Greenlink | PINT | 19 | 56 | 0 | -3 | 0 | -6 | 88 | 94 | 77 | 38 | 79 | 4 | 1 | 0 | 0 | 1294 | 1432 | 1209
293 | Southern Aegean Interconnector | PINT | 88 | 91 | 86 | 27 | 28 | 24 | 78 | 91 | 65 | -340 | -305 | -363 | 0 | 7 | 38 | 1104 | 1178 | 1020
297 | BRABO II + III | TOOT | 34 | 40 | 24 | 7 | 9 | 4 | 29 | 36 | 23 | -85 | -55 | -111 | 0 | 2 | 9 | 372 | 453 | 299
299 | SACOI3 | TOOT | 125 | 138 | 106 | 31 | 37 | 26 | 77 | 88 | 68 | -396 | -331 | -469 | 0 | 9 | 44 | 988 | 1108 | 888
309 | NeuConnect | TOOT | -9 | 0 | -28 | -44 | -37 | -49 | 26 | 29 | 23 | 593 | 694 | 473 | 10 | 0 | 0 | 341 | 387 | 294
312 | St. Peter (AT) - Tauern (AT) | TOOT | 206 | 271 | 108 | 70 | 80 | 60 | 28 | 36 | 18 | -923 | -771 | -1088 | 0 | 20 | 99 | 358 | 458 | 238
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | TOOT | 247 | 271 | 185 | 72 | 80 | 60 | 26 | 36 | 18 | -986 | -800 | -1088 | 0 | 20 | 102 | 358 | 458 | 238
323 | Dekani (SI) - Zaule (IT) interconnection | TOOT | 1 | 5 | 0 | 0 | 5 | -4 | 2 | 6 | 0 | -1 | 52 | -58 | 0 | 0 | 0 | 20 | 75 | 0
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | TOOT | 2 | 5 | 0 | -1 | 0 | -3 | 4 | 11 | 0 | 18 | 36 | -1 | 0 | 0 | 0 | 55 | 137 | -1
325 | Obersielach (AT) - Podlog (SI) | PINT | 33 | 42 | 24 | 13 | 19 | 10 | 4 | 7 | 2 | -170 | -125 | -248 | 0 | 4 | 19 | 57 | 91 | 28
328 | Interconnector DE-LUX | TOOT | 6 | 9 | 1 | -3 | 0 | -6 | 4 | 14 | 1 | 34 | 71 | 1 | 1 | 0 | 0 | 56 | 169 | 13
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
330 | 4th 400kV CZ-SK interconnector | light PINT | 14 | 17 | 12 | 8 | 12 | 5 | 1 | 2 | 0 | -106 | -62 | -159 | 0 | 2 | 12 | 18 | 25 | 5
333 | PST Foretaille | PINT | 169 | 183 | 161 | 71 | 86 | 59 | 14 | 17 | 12 | -911 | -758 | -1103 | 0 | 20 | 101 | 182 | 220 | 147
335 | North Sea Wind Power Hub | light PINT | 1682 | 1693 | 1672 | 1058 | 1074 | 1042 | 4414 | 4414 | 4414 | -13559 | -13355 | -13764 | 0 | 298 | 1505 | 55903 | 55917 | 55890
338 | Adriatic HVDC link | PINT | 131 | 136 | 125 | 33 | 35 | 30 | 75 | 86 | 65 | -441 | -431 | -450 | 0 | 9 | 46 | 975 | 1104 | 846
339 | Tyrrhenian link | PINT | 93 | 124 | 53 | 26 | 30 | 24 | 95 | 95 | 94 | -354 | -303 | -432 | 0 | 7 | 38 | 1138 | 1214 | 999
340 | Avelgem-Courcelles (Boucle du Hainaut): new corridor | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341 | North CSE Corridor | PINT | 53 | 60 | 50 | 30 | 34 | 28 | 26 | 28 | 24 | -396 | -368 | -435 | 0 | 8 | 43 | 334 | 360 | 304
342 | Central Balkan Corridor | PINT | 31 | 35 | 26 | 4 | 15 | -6 | 12 | 17 | 8 | -55 | 81 | -188 | 0 | 1 | 6 | 154 | 222 | 103
343 | CSE1 New | PINT | 9 | 12 | 6 | 1 | 5 | -1 | 3 | 6 | 0 | -16 | 12 | -66 | 0 | 0 | 2 | 38 | 83 | 5
346 | ZuidWest380 NL Oost | PINT | 28 | 31 | 26 | -2 | 1 | -5 | 17 | 21 | 12 | 21 | 61 | -8 | 0 | 0 | 0 | 224 | 269 | 150
349 | MaresConnect | PINT | 0 | 0 | 0 | -3 | 1 | -6 | 137 | 145 | 131 | 45 | 83 | -14 | 1 | 0 | 0 | 1770 | 1843 | 1720
350 | South Balkan Corridor | TOOT | 26 | 29 | 21 | -5 | -4 | -6 | 10 | 12 | 8 | 65 | 78 | 48 | 1 | 0 | 0 | 138 | 147 | 122
375 | Lienz (AT) - Veneto region (IT) 220 kV | PINT | 68 | 86 | 49 | 11 | 14 | 6 | 9 | 15 | 3 | -149 | -92 | -182 | 0 | 3 | 16 | 111 | 186 | 33
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | light PINT | 3 | 3 | 3 | -3 | -1 | -6 | 5 | 11 | 0 | 44 | 72 | 18 | 1 | 0 | 0 | 60 | 137 | 5
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | PINT | 26 | 27 | 26 | -2 | 1 | -5 | 23 | 28 | 19 | 30 | 61 | -8 | 1 | 0 | 0 | 291 | 351 | 254
378 | Transformer Gatica | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379 | Uprate Gatica lines | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1034 | HVDC corridor from Northern Germany to Western Germany | PINT | 7224 | 7224 | 7224 | 170 | 170 | 170 | 1276 | 1276 | 1276 | -6081 | -6081 | -6081 | 0 | 134 | 675 | 12756 | 12756 | 12756
1039 | SE North-south long-term reinforcements | light PINT | 29 | 46 | 14 | 12 | 18 | 5 | 12 | 26 | 1 | -148 | -70 | -234 | 0 | 3 | 16 | 153 | 337 | 16
1040 | LirIC | PINT | 4 | 10 | 0 | -6 | -4 | -10 | 101 | 103 | 99 | 81 | 125 | 47 | 1 | 0 | 0 | 1376 | 1498 | 1293
1041 | GREGY Green Energy Interconnector | PINT | 319 | 326 | 307 | -199 | -37 | -389 | 85 | 99 | 71 | 2689 | 5564 | 479 | 46 | 0 | 0 | 1099 | 1288 | 921
1042 | Offshore Wind LT 1 | PINT | 55 | 63 | 49 | 7 | 16 | 2 | 133 | 147 | 115 | -86 | -28 | -210 | 0 | 2 | 9 | 1757 | 1905 | 1668
1046 | Finnish North-South reinforcement | PINT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1047 | Emden-Eemshaven | light PINT | 56 | 69 | 40 | 8 | 12 | 4 | 16 | 20 | 12 | -101 | -56 | -155 | 0 | 2 | 11 | 202 | 259 | 162
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | PINT | 599 | 612 | 590 | -38 | 0 | -86 | 688 | 694 | 684 | 518 | 1229 | -3 | 9 | 0 | 0 | 8968 | 9069 | 8877
1049 | Cronos Energy Ltd | PINT | 0 | 0 | 0 | -44 | -39 | -49 | 17 | 18 | 16 | 568 | 632 | 503 | 10 | 0 | 0 | 217 | 238 | 196
1050 | Tarchon Energy Ltd | PINT | 0 | 0 | 0 | -55 | -53 | -57 | 24 | 32 | 17 | 702 | 731 | 674 | 13 | 0 | 0 | 309 | 413 | 229
1051 | Aminth Energy Ltd | PINT | 0 | 0 | 0 | -13 | -13 | -13 | 192 | 192 | 192 | 168 | 169 | 168 | 3 | 0 | 0 | 2520 | 2520 | 2520
1052 | Lienz (AT) - Obersielach (AT) | PINT | 31 | 36 | 24 | 13 | 19 | 10 | 8 | 14 | 4 | -165 | -122 | -248 | 0 | 4 | 18 | 108 | 175 | 58
1054 | Westtirol (AT) - Zell/Ziller (AT) | PINT | 60 | 71 | 51 | 15 | 21 | 9 | 8 | 17 | 4 | -188 | -117 | -270 | 0 | 4 | 21 | 108 | 217 | 59
1055 | Interconnection of Crete to the Mainland System of Greece | TOOT | 394 | 404 | 382 | 97 | 100 | 95 | 341 | 351 | 333 | -1249 | -1219 | -1279 | 0 | 27 | 139 | 4399 | 4438 | 4347
1058 | HVDC Interconnector DE-CH | light PINT | 121 | 136 | 110 | 31 | 35 | 24 | 18 | 24 | 15 | -395 | -305 | -444 | 0 | 9 | 44 | 234 | 299 | 195
1059 | Southern Italy | PINT | 6 | 9 | 5 | 2 | 2 | 0 | 9 | 11 | 7 | -21 | 3 | -32 | 0 | 0 | 2 | 117 | 141 | 84
1066 | Bulgaria - Turkey | light PINT | 118 | 128 | 110 | -164 | -133 | -204 | 27 | 41 | 16 | 2109 | 2612 | 1705 | 38 | 0 | 0 | 345 | 537 | 211
1067 | New AC 400 kV interconnection line Greece - Turkey | light PINT | 64 | 65 | 61 | -72 | -56 | -88 | 33 | 38 | 27 | 926 | 1122 | 720 | 17 | 0 | 0 | 420 | 500 | 346
1068 | LaSGo Link | light PINT | 53 | 54 | 52 | 14 | 16 | 13 | 25 | 33 | 15 | -179 | -167 | -201 | 0 | 4 | 20 | 348 | 425 | 268
1074 | Pannonian Corridor | PINT | 16 | 22 | 11 | 8 | 12 | 4 | 2 | 3 | 1 | -104 | -52 | -151 | 0 | 2 | 12 | 29 | 44 | 17
1082 | Sea-Socket | light PINT | 97 | 126 | 74 | 26 | 28 | 23 | 148 | 152 | 145 | -335 | -291 | -365 | 0 | 7 | 37 | 1904 | 1919 | 1885
1085 | Malta-Italy Cable Link No.2 | PINT | 2 | 5 | 0 | -15 | -14 | -16 | 1 | 1 | 1 | 193 | 205 | 173 | 3 | 0 | 0 | 14 | 15 | 12
1086 | Estonia internal grid reinforcement to increase RES connection capability (RRF project) | PINT | 56 | 66 | 51 | 10 | 16 | 5 | 105 | 128 | 85 | -131 | -66 | -207 | 0 | 3 | 15 | 1470 | 1615 | 1329
1088 | Latvia and Estonia Hybrid Off-Shore interconnector | PINT | 14 | 24 | 6 | 7 | 8 | 6 | 181 | 217 | 147 | -92 | -80 | -103 | 0 | 2 | 10 | 2542 | 2741 | 2350
1092 | Triton Link: offshore hybrid HVDC interconnector Belgium – Denmark | PINT | 447 | 491 | 402 | 211 | 214 | 208 | 840 | 966 | 715 | -2710 | -2669 | -2750 | 0 | 60 | 301 | 12257 | 12288 | 12227
1094 | Estlink 3 | light PINT | 68 | 75 | 60 | 21 | 25 | 17 | 47 | 47 | 47 | -275 | -213 | -322 | 0 | 6 | 31 | 579 | 614 | 526
1095 | Aurora line 2 (4th AC Finland-Sweden north) | light PINT | 57 | 68 | 48 | 5 | 7 | 3 | 57 | 65 | 47 | -69 | -33 | -94 | 0 | 2 | 8 | 802 | 825 | 779
1096 | Beznau - Mettlen | PINT | 55 | 59 | 51 | 19 | 20 | 17 | 11 | 13 | 7 | -238 | -223 | -261 | 0 | 5 | 26 | 143 | 171 | 113
1097 | Upgrade to Konti-Skan | PINT | 171 | 175 | 166 | 41 | 49 | 30 | 51 | 59 | 40 | -520 | -383 | -628 | 0 | 11 | 58 | 650 | 747 | 516
1098 | Offshore Wind LT 2 | PINT | 55 | 63 | 49 | 9 | 16 | 2 | 128 | 137 | 115 | -109 | -28 | -210 | 0 | 2 | 12 | 1650 | 1737 | 1503
1100 | Reinforcement of the existing CZ-DE interconnector (Hradec - Röhrsdorf) on the CZ side | PINT | 28 | 29 | 26 | 17 | 18 | 17 | 14 | 17 | 11 | -224 | -220 | -228 | 0 | 5 | 25 | 183 | 217 | 150
1102 | Mettlen - Ulrichen | light PINT | 19 | 21 | 18 | 5 | 7 | 3 | 4 | 7 | 2 | -67 | -38 | -85 | 0 | 1 | 7 | 52 | 88 | 30
1103 | Bickigen - Chippis | PINT | 42 | 43 | 40 | 13 | 15 | 9 | 6 | 10 | 5 | -163 | -111 | -196 | 0 | 4 | 18 | 90 | 125 | 61
1104 | Niederstedem - Roost | PINT | 1 | 3 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | -18 | 0 | -31 | 0 | 0 | 2 | 6 | 12 | 0
1105 | Georgia-Romania Black Sea (submarine) interconnection cable project | PINT | 113 | 113 | 113 | -50 | -50 | -50 | 41 | 42 | 40 | 643 | 645 | 641 | 12 | 0 | 0 | 531 | 550 | 512
1106 | Bornholm Energy Island (BEI) | TOOT | 353 | 355 | 652 | 225 | 240 | 204 | 626 | 636 | 616 | -2882 | -2620 | -3075 | 0 | 63 | 320 | 8075 | 8117 | 8048
1107 | EuroAfrica Interconnector | PINT | 67 | 70 | 65 | 24 | 44 | 6 | 36 | 43 | 30 | -307 | -71 | -569 | 0 | 7 | 34 | 468 | 550 | 394
1109 | Basilicata - Campania reinforcements | PINT | 16 | 19 | 11 | 2 | 4 | 0 | 21 | 27 | 12 | -30 | -6 | -64 | 0 | 1 | 3 | 268 | 334 | 151
1110 | Sicily - Calabria | PINT | 6 | 9 | 2 | 1 | 3 | -1 | 5 | 11 | 1 | -14 | 8 | -35 | 0 | 0 | 2 | 63 | 136 | 14
1112 | GRITA 2 | PINT | 80 | 85 | 76 | 26 | 29 | 20 | 53 | 56 | 47 | -345 | -261 | -385 | 0 | 7 | 37 | 688 | 734 | 613
1119 | Bisamberg (AT) - Wien SO (AT) - Parndorf (AT) | PINT | 491 | 491 | 491 | 145 | 145 | 145 | 527 | 527 | 527 | -1861 | -1861 | -1861 | 0 | 41 | 207 | 6831 | 6831 | 6831
1120 | Wien SO (AT) – Ternitz (AT) – Hessenberg (AT) | PINT | 138 | 138 | 138 | 40 | 40 | 40 | 132 | 132 | 132 | -511 | -511 | -511 | 0 | 11 | 57 | 1708 | 1708 | 1708
1121 | Hessenberg (AT) - Weißenbach (AT) | PINT | 112 | 112 | 112 | 33 | 33 | 33 | 95 | 95 | 95 | -418 | -418 | -418 | 0 | 9 | 46 | 1232 | 1232 | 1232
1122 | Offshore Wind connection Centre Manche 1 | TOOT | 282 | 282 | 281 | 57 | 66 | 51 | 386 | 388 | 384 | -735 | -657 | -848 | 0 | 16 | 82 | 5072 | 5152 | 5016
1123 | Offshore Wind Connection Centre Manche 2 | PINT | 282 | 282 | 281 | 60 | 66 | 55 | 397 | 407 | 388 | -775 | -701 | -848 | 0 | 17 | 86 | 5101 | 5152 | 5049
1124 | Offshore Wind Connection South Britanny | TOOT | 171 | 173 | 169 | 31 | 39 | 23 | 235 | 238 | 233 | -402 | -296 | -494 | 0 | 9 | 45 | 3035 | 3048 | 3021
1125 | Offshore Wind Connection Occitanie | TOOT | 171 | 173 | 169 | 31 | 39 | 23 | 235 | 238 | 233 | -402 | -296 | -494 | 0 | 9 | 45 | 3035 | 3048 | 3021
1126 | Offshore Wind Connection PACA | TOOT | 171 | 173 | 169 | 31 | 39 | 23 | 235 | 238 | 233 | -402 | -296 | -494 | 0 | 9 | 45 | 3035 | 3048 | 3021
1127 | Offshore Wind Connection South Atlantic | PINT | 274 | 284 | 264 | 54 | 60 | 46 | 385 | 387 | 382 | -698 | -594 | -767 | 0 | 15 | 77 | 5087 | 5222 | 4992
1129 | New RES at Minho region | TOOT | 43 | 44 | 42 | 10 | 12 | 7 | 50 | 51 | 49 | -122 | -90 | -153 | 0 | 3 | 14 | 648 | 651 | 641

## Trans.ProjectLevelBenefits
Project ID | Project name | B7.1 Balancing Energy Exchange | [5 empty] | B8.1 Frequency stability | [5 empty] | B8.2 Blackstart services: Methodology for Synchronisation with Continental Europe | [5 empty] | B9 Reduction of necessary reserve for re-dispatch power plants
|  | NT2030 | NT2040 | DE2030 | DE2040 | 2030 | 2040 | NT2030 | NT2040 | DE2030 | DE2040 | 2030 | 2040 | NT2030 | NT2040 | DE2030 | DE2040 | 2030 | 2040 | NT2030 |  | NT2040 |  | DE2030 |  | DE2040 |  | 2030 | 2040
|  | Qualitative assessment by ENTSO-E | [5 empty] | MWh/year | [5 empty] | M€ / year | [5 empty] | M€ / year |  | M€ / year |  | M€ / year |  | M€ / year |  | M€ / year | M€ / year
1 | RES in north of Portugal
4 | Interconnection Portugal-Spain | + |  | +
16 | Biscay Gulf
26 | Reschenpass Interconnector Project
28 | Italy-Montenegro | + | +
29 | Italy-Tunisia
33 | Central Northern Italy
35 | CZ Southwest-east corridor
40 | Belgium-Luxembourg-Germany: long-term perspective
47 | Westtirol (AT) - Vöhringen (DE)
81 | North South Interconnector
85 | Integration of RES in Alentejo
94 | GerPol Improvements
103 | Reinforcements Ring NL phase I
107 | Celtic Interconnector
111 | Aurora line (3rd AC Finland-Sweden north)
120 | Belgian Modular Offshore Grid II (MOG II)
121 | Nautilus: multi-purpose interconnector Belgium - UK
123 | LitPol Link Stage 2
124 | NordBalt phase 2
126 | SE North-south short-term reinforcements
127 | Central Southern Italy
130 | HVDC SuedOstLink Wolmirstedt to area Isar | [18 empty] | 50.75 | 2.54 GW |  | GW | 66.61 | 3.33 GW | 53.84 | 2.69 GW
132 | HVDC Line A-North | [18 empty] | 67.10 | 3.36 GW |  | GW | 111.48 | 5.58 GW | 106.24 | 5.31 GW
138 | Black Sea Corridor
142 | CSE4
144 | Mid Continental East corridor
150 | Italy-Slovenia
153 | France-Alderney-Britain
170 | Baltic States Synchronization with Continental Europe
174 | Greenconnector
176 | Hansa PowerBridge I
183 | DKW-DE, Westcoast
186 | East of Austria
187 | St. Peter (AT) - Pleinting (DE)
190 | NorthConnect
200 | CZ Northwest-South corridor
210 | Würmlach (AT) - Somplago (IT) interconnection
219 | EuroAsia Interconnector
225 | 2nd interconnector Belgium - Germany | [10 empty] | max. RoCoF can be reduced by 130 mHz/s with the 2nd IC | max. RoCoF can be reduced by 200 mHz/s with the 2nd IC
227 | Transbalkan Corridor
228 | Muhlbach - Eichstetten
230 | GerPol Power Bridge I
231 | Beznau - Tiengen
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Bergrheinfeld West | [18 empty] | 110.25 | 5.51 GW |  | GW | 150.90 | 7.55 GW | 139.12 | 6.96 GW
239 | Fenno-Skan 1 renewal
243 | New 400 kV interconnection line between Serbia and Croatia
244 | Vigy - Uchtelfangen area
247 | AQUIND Interconnector
250 | Merchant line Castasegna (CH) - Mese (IT)
252 | Internal Belgian Backbone Center-East: HTLS upgrade Massenhoven-VanEyck-Gramme-Courcelles-Bruegel-Mercator
253 | Upstream reinforcement in France to increase FR-CH capacity
254 | HVDC Ultranet Osterath to Philippsburg | [18 empty] | 14.10 | 0.71 GW |  | GW | 28.41 | 1.42 GW | 3.09 | 0.15 GW
259 | HU-RO
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands
263 | Lake Constance East
267 | Hansa PowerBridge II
270 | FR-ES project -Aragón-Atlantic Pyrenees
276 | FR-ES project -Navarra-Landes
280 | FR-BE: study Lonny-Achene-Gramme
283 | TuNur Italy
285 | GridLink
286 | Greenlink
293 | Southern Aegean Interconnector
297 | BRABO II + III
299 | SACOI3 | ++ | ++
309 | NeuConnect
312 | St. Peter (AT) - Tauern (AT)
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT)
323 | Dekani (SI) - Zaule (IT) interconnection
324 | Redipuglia (IT) - Vrtojba (SI) interconnection
325 | Obersielach (AT) - Podlog (SI)
328 | Interconnector DE-LUX
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor
330 | 4th 400kV CZ-SK interconnector
333 | PST Foretaille
335 | North Sea Wind Power Hub
338 | Adriatic HVDC link | ++ | ++
339 | Tyrrhenian link | ++ | ++
340 | Avelgem-Courcelles (Boucle du Hainaut): new corridor
341 | North CSE Corridor
342 | Central Balkan Corridor
343 | CSE1 New
346 | ZuidWest380 NL Oost
349 | MaresConnect
350 | South Balkan Corridor
375 | Lienz (AT) - Veneto region (IT) 220 kV | ++ | ++
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht
378 | Transformer Gatica
379 | Uprate Gatica lines
1034 | HVDC corridor from Northern Germany to Western Germany | [18 empty] | 44.22 | 2.21 GW |  | GW | 127.71 | 6.38 GW | 75.41 | 3.77 GW
1039 | SE North-south long-term reinforcements
1040 | LirIC
1041 | GREGY Green Energy Interconnector | ++ | [17 empty] | 4,2 - 14,7 | 71.15 - 250.46 MW Average redispatch decrease with GREGY: 71.15 - 250.46 MW |  | Average redispatch decrease with GREGY: 71.15 - 250.46 MW |  | Average redispatch decrease with GREGY: 71.15 - 250.46 MW |  | Average redispatch decrease with GREGY: 71.15 - 250.46 MW
1042 | Offshore Wind LT 1
1046 | Finnish North-South reinforcement
1047 | Emden-Eemshaven
1048 | Greece - Africa Power Interconnector (GAP Interconnector)
1049 | Cronos Energy Ltd
1050 | Tarchon Energy Ltd
1051 | Aminth Energy Ltd
1052 | Lienz (AT) - Obersielach (AT)
1054 | Westtirol (AT) - Zell/Ziller (AT)
1055 | Interconnection of Crete to the Mainland System of Greece
1058 | HVDC Interconnector DE-CH
1059 | Southern Italy | ++ | ++
1066 | Bulgaria - Turkey
1067 | New AC 400 kV interconnection line Greece - Turkey
1068 | LaSGo Link
1074 | Pannonian Corridor
1082 | Sea-Socket
1085 | Malta-Italy Cable Link No.2
1086 | Estonia internal grid reinforcement to increase RES connection capability (RRF project)
1088 | Latvia and Estonia Hybrid Off-Shore interconnector
1092 | Triton Link: offshore hybrid HVDC interconnector Belgium – Denmark
1094 | Estlink 3
1095 | Aurora line 2 (4th AC Finland-Sweden north)
1096 | Beznau - Mettlen
1097 | Upgrade to Konti-Skan
1098 | Offshore Wind LT 2
1100 | Reinforcement of the existing CZ-DE interconnector (Hradec - Röhrsdorf) on the CZ side
1102 | Mettlen - Ulrichen
1103 | Bickigen - Chippis
1104 | Niederstedem - Roost
1105 | Georgia-Romania Black Sea (submarine) interconnection cable project
1106 | Bornholm Energy Island (BEI)
1107 | EuroAfrica Interconnector
1109 | Basilicata - Campania reinforcements | + | ++
1110 | Sicily - Calabria | ++ | ++
1112 | GRITA 2
1119 | Bisamberg (AT) - Wien SO (AT) - Parndorf (AT)
1120 | Wien SO (AT) – Ternitz (AT) – Hessenberg (AT)
1121 | Hessenberg (AT) - Weißenbach (AT)
1122 | Offshore Wind connection Centre Manche 1
1123 | Offshore Wind Connection Centre Manche 2
1124 | Offshore Wind Connection South Britanny
1125 | Offshore Wind Connection Occitanie
1126 | Offshore Wind Connection PACA
1127 | Offshore Wind Connection South Atlantic
1129 | New RES at Minho region

## Stor.ProjectLevelBenefits
Project ID | Project name | B7 System flexibility |  |  |  | B7.1 Balancing Energy Exchange | [5 empty] | B8.2 Blackstart services: Methodology for Synchronisation with Continental Europe | [5 empty] | B9 Reduction of necessary reserve for re-dispatch power plants
|  | Response time FCR | Response time - Including delay of IT and control ssytems | Duration at rated power | Available power | NT2030 | NT2040 | DE2030 | DE2040 | 2030 | 2040 | NT2030 | NT2040 | DE2030 | DE2040 | 2030 | 2040 | NT2030 | NT2040 | DE2030 | DE2040 | 2030 | 2040
[6 empty] | Qualitative assessment by ENTSO-E | [5 empty] | M€ / year | [5 empty] | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year